## DESC Projects
Project ID | Project Name / Endpoints (raw title) | Description | Need / Area Note | Status | Planned In-Service Date
6807 B | Queensboro - Ft Johnson 115 kV & Queensboro-Bayfront 115kV (Queensboro-James Island Sect) | Replace the Queensboro – Ft Johnson 115 kV Line and structures as they have reached the end of life. | This project is required due to address end of life issues. | In Progress | 12/31/23
0167C-D | Union Pier 115-13.8 kV Sub: Tap | Installing a 115 kV Tap to feed the future Union Pier 115 kV Sub. | This project is needed to for load growth in the Charleston area. | Planned | 12/31/27
0139 M,N | Okatie 230-115kV Substation, Jasper – Yemassee 230kV #1 Fold-in | Expand existing Okatie Transmission sub, add a 230-115 autobank and fold the Jasper – Yemassee 230 kV #1 line into the 230 kV side. Construct two additional 115 kV bus tie lines. | This project is needed to improve system performance and to meet NERC TPL and internal DESC Planning Criteria for reliability. | In Progress | 12/31/2024
6341 A-F | Cainhoy - Hamlin 115kV: Rebuild Line and Cainhoy – Hamlin 115 kV #2: Construct New 115 kV Line | Upgrade the 954 ACSR portion of the Cainhoy – Hamlin 115 kV line to B795 ACSR conductor, construct a new Cainhoy – Hamlin 115 kV #2 line, add terminals to Cainhoy and Hamlin sub to accommodate upgrades. | This project is required due to load growth in the Mount Pleasant area and to meet NERC TPL and internal DESC Planning criteria. | In Progress | 12/01/25
6808 J | Eastover - Square D 115kV: Rebuild | Replace wooden H-Frame structures with Self Supporting Steel Structures and restring with 1272 ACSR conductor. | This project is required to address end of life and reliability issues on these lines. | In Progress | 06/01/24
6808 K | Burton-St Helena 115kV: Rebuild Burton-Frogmore Transmission Section | Replace wooden structures with Self Supporting Steel Structures and restring with 1272 ACSR conductor for the Burton – Frogmore Transmission section. | This project is required to address end of life and reliability issues on these lines. | In Progress | 12/31/24
6808 L | Burton-St Helena 115kV: Frogmore Distribution - St Helena | Replace wooden structures with Self Supporting Steel Structures and upgrade to 795 ACSR for the Frogmore Distribution Tap – St. Helena section. | This project is required to address end of life and reliability issues on these lines. | In Progress | 12/31/25
6808 N,O | VCS1-Denny Terrace 230kV & VCS1-Pineland 230kV: Rebuild Single Circuit Sections | Replace wooden H-Frame structures with Self Supporting Steel Structures and restring with standard 1272 ACSR conductor. | This project is required to address end of life and reliability issues on these lines. | In Progress | 12/31/26
6808 R | Wateree-Killian 230kV: Rebuild | Replace wooden H-Frame structures with Self Supporting Steel Structures. | This project is required to address end of life and reliability issues on these lines. | In Progress | 12/31/28
6808 S | Okatie-Bluffton 115kV: Rebuild | Replace wooden H-Frame structures with Self Supporting Steel Structures and upgrade conductor to standard 1272 ACSR. | This project is required to address end of life and reliability issues on these lines. | In Progress | 06/01/2025
6808 U | Hopkins-CIP 230kV: Rebuild | Replace wooden H-Frame structures with Self Supporting Steel Structures. | This project is required to address end of life and reliability issues on these lines. | Planned | 12/31/25
6808 V | Faber Place-Bayfront 115kV: Rebuild North Bridge Terrace to Bayfront Section | Replace wooden structures with Self Supporting Steel Structures and upgrade conductor to standard 1272 ACSR. | This project is required to address end of life and reliability issues on these lines. | Planned | 12/31/28
6808 W | Square D - Hopkins 115kV: Rebuild | Replace wooden H-Frame structures with Self Supporting Steel Structures and restring with 1272 ACSR conductor. | This project is required to address end of life and reliability issues on these lines. | In Progress | 9/30/2024
6809 E | Stevens Creek - Hooks 115kV/LR Plumb Branch 46kV Rebuilds | 9.5 miles. Scope includes rebuilding the 115 and 46 kV lines in this corridor SPDC. | This project is required to address end of life and reliability issues on these lines. | In Progress | 12/31/24
6809 G | Stevens Creek - Hooks 115kV/LR Plumb Branch 46kV | Upgrade 6.5 miles of aging conductor with 1272 ACSR and rebuild with SPDC. | This project is required to address end of life and reliability issues on these lines. | Planned | 12/31/25
6805 G | Edenwood Sub: #1 & #2 230-115kV Autobanks, Replace with 336MVA | Replace Autobank 1 and 2 at Edenwood Substation. | This project is required to address end of life and maintenance issues on these transformers. | In Progress | 12/25/24
1060A, I, L | Williams St Sub: Replace Sw House & Relays, AM Williams Sub: Replace Sw House, and McMeekin Sub: Add Sw House | Replace switch house, switch house equipment, and relay panels at Williams Street substation. Replace the switch house at AM Williams substation. Add Switching House at McMeekin Substation to move relays from plant relay room. | This project is required to address end of life and maintenance issues on these transformers. | In Progress | 12/31/28
06005 B | Harleyville 115KV Transmission Tap – Construct (1.4 miles) | Extend the 115 kV line from the Blue Circle tap to the Harleyville substation to provide 115 kV service. | Load growth. | Planned | 3/31/2027
05004 P | Summerville: Replace and Spare 230-115kV 336MVA Auto Bank | Purchase a spare 230/115kV, 336MVA Autobank for the Southern Region to be stored at Summerville 230kV Sub. Include a pad, AC for heaters, and possibly a pit for oil containment. | Spare equipment needs. | In Progress | 12/31/2024
06076A | Canadys-Ritter 115KV-Rebld SPDC 230/115KV 1272 (Approx 18 Miles) | Rebuild Canadys-Ritter 115 kV line as SPDC with 230 kV on one side and 115 kV on the other side. | This project is needed to improve system performance and to meet NERC TPL and internal DESC Planning Criteria for reliability. | In Progress | 6/1/2026
6359 | Yemassee– Ritter 230kV #1 & #2: Construct SPDC with B-1272 | Construct Ritter – Yemassee 230kV #1 and #2 SPDC with B1272 ACSR on both sides. Convert the existing Ritter – Yemassee 230 kV to 115 kV operation. Convert and add terminals at Ritter and Yemassee. Add 230 kV bus tie at Ritter and upgrade the Yemassee 230 kV bus tie. | This project is needed to improve system performance and to meet NERC TPL and internal DESC Planning Criteria for reliability. | Planned | 6/1/2026
06367 A - C, H | Riverport Tap: Construct Tap | Construct Okatie – Riverport 230 kV to feed new Distribution substation. | Load growth. | In Progress | 12/31/25
06367 D - G | Jasper – Okatie 230 kV #2: Construct | Construct a 230 kV line with B1272 ACSR from Jasper to Okatie 230/115kV Substation. The line is estimated to be 6.5 miles long. This makes Jasper a Medium Impact substation and will require a new CIP Hut. | This project is needed to improve system performance and to meet NERC TPL and internal DESC Planning Criteria for reliability. | In Progress | 12/31/25
06371 D | Wagener 115kV Tap: Construct Tap | Constructing a 115 kV Tap off the Edmund Switching Station- Owens Corning 115 kV Line to feed new Wagener Distribution substation. | Load growth. | Planned | 12/31/25
06372 A | Church Creek - Ritter 230kV - Replace 38 Large Angles and Dead Ends | Replace 6.5 miles of aging conductor. | Replacing approximately 38 guyed wooden structures due to recent failures in the fiberglass strain insulators along this line. Structures to be changed out are dead ends/large angles. | In Progress | 6/1/2024
06810 F | VCS2-Ward 230kV: Rebuild Line | Rebuild 40 miles of 230 kV line. | This project is required to address end of life and maintenance issues. | Planned | 12/31/29
06810 G | Goose Creek Reservoir: Rebuild Transmission Line Crossings | Rebuilding the Williams Goose Creek 230 and 115 kV lines and the Williams - Faber Place 230 kV line across the Goose Creek Reservoir. | This project is required to address end of life and maintenance issues. | In Progress | 12/31/24
06810 H | Summerville 115kV Loop: Rebuild | Replacing several wood pole sections on the Summerville 115 kV Loop that have reached the end of life. | This project is required to address end of life and maintenance issues. | In Progress | 12/31/24
6809 M | St George - Sumter 230kV Tie: Rebuild Line from Santee Substation - Duke/Progress Energy Tie | Rebuild Line from Santee Substation - Duke/Progress Energy Tie. | Grid hardening. | Planned | 12/31/2025
5392 A-C | Coit – Gills Creek 115kV: Construct | Convert the existing Coit - Gills Creek 33 kV Line to 115 kV. Approximately 1.25 miles. Construct Gills Creek Terminal at Coit Bus #1. | Load growth. | In Progress | 12/31/2024
6810 A | Hooks - Thurmond 115kV Tie: Rebuild | Rebuilding section of line between Hooks and Thurmond. Approximately 2.3 miles. The line will be rebuilt on existing R/W using steel poles, 115 kV insulation, and 1272 ACSR conductor. | This project is required to address end of life and reliability issues on these lines. | In Progress | 12/31/2024
6809 N | Batesburg - Saluda County 115kV: Rebuild | Rebuild 13.5 miles of conductor. | Grid hardening. | In Progress | 12/31/2025
6853 B-F | Scout 230 kV Sub and Fold-in: Construct | Construct 230kV Transmission Line for Scout Customer Substation and modify VCS1 and Killian terminals. | Load growth. | In Progress | 3/31/2026
6859 | Dawson 230kV Sub and Fold-in: Construct and Rebuild | Construct Dawson 230kV substation. Fold in the existing Canadys – Church Creek and Canadys – Faber Place 230kV lines at the Dawson 230kV substation (phase 1). Rebuild Canadys – Dawson 230kV #1 and #2 with B1272 ACSR (phase 2). | Load growth. | In Progress | 10/1/2025 (phase 1) and 10/1/2026 (phase 2)
6852 | Urquhart – Toolebeck 115kV line: Rebuild | Upgrade the 477 ACSR portions of the Urquhart – Toolebeck 115 kV line to 1272 ACSR. Replace existing structures with Single Pole Double Circuit Structures. Approximately 12.5 miles. | This project is needed to improve system performance and to meet NERC TPL and internal DESC Planning Criteria for reliability. | In Progress | 8/12/2026
6388 A | Williams-Summerville 230kV: Upgrade to SPDC B1272 ACSR | Rebuild the section of the Williams - Summerville 230 kV line from Ladson Jct to Williams. Line to upgraded to B-1272 and designed for a future second circuit. Approximately 10 miles. | This project is needed to improve system performance and to meet NERC TPL and internal DESC Planning Criteria for reliability. | Planned | 5/1/2027
0147 C, K | Cainhoy 115 kV Tap: Construct | Construct a 115 kV tap from Cainhoy to Clements Ferry. Approximately 2.8 miles. Construct terminal at Cainhoy. | Load growth. | Planned | 12/31/2027
0147 B, J | Jack Primus 115 kV Tap: Construct | Construct a 115 kV tap from Jack Primus to Clements Ferry. Approximately 2.2 miles. Construct terminals at Jack Primus. | Load growth. | Planned | 12/31/2027
6847 A-B, D-H | Church Creek – Faber Place – Charleston Transmission: Add 230kV Line | Construct a 230 kV transmission line from Church Creek to Charleston Transmission. The Church Creek – Faber Place 230kV and 115kV lines will be rebuilt, and a 230kV line will be added between Faber Place and Charleston Transmission. Add 230/115kV transformer at Charleston Transmission. Add/upgrade terminals and bus work at impacted substations. | This project is needed to improve system performance and to meet NERC TPL and internal DESC Planning Criteria for reliability. | In Progress | 05/01/2027
6846 A | Eastover – Sumter 115kV DEP Tie: Rebuild with 1272 ACSR | Upgrade the DESC section (approx. 1 mile) of the tie line from 397.5 ACSR Ibis to 1272 ACSR. | This project is needed to improve system performance and to meet NERC TPL and internal DESC Planning Criteria for reliability. | Planned | 05/31/2026
6810 U | Cameron Jct – Elloree 46 kV Rebuild | Rebuilding the Cameron Jct – Elloree 46 kV Line. 7.3 miles. | System hardening | Planned | 12/31/2026
6810 J | Elloree – Santee City 46 kV: Rebuild | Rebuilding the 46 kV line between Elloree and Santee City. 7 miles. | System hardening | Planned | 12/31/2027
6810 O | Urquhart – Aiken PSA 46 kV: Rebuild | Rebuilding the section of 46 kV line from Urquhart to the Aiken PSA tap point. TBD if the scope of this project includes rebuilding the actual tap Aiken PSA. 4.5 miles. | System hardening | Planned | 12/31/2027
6810 T | Cameron Jct – Cameron – St Matthews 46 kV Rebuild | Rebuilding the 46 kV line between Cameron Jct and St Matthews. 9.8 miles. | System hardening. | Planned | 12/31/2028

## GA ITS Projects
Zone | TEAMS Number | Project Name / Endpoints (raw title) | Sponsor (GPC/GTC/MEAG/DU/SAV) | Year Filed | Need / In-Service Date
216 | 19631 | PINE GROVE PRIMARY 115 KV DUAL STAGE CAPACITOR BANK | GPC | 2025 | 6/1/2025
219 | 20067 | SAV: DEPTFORD - MAGNOLIA 115KV RECONDUCTOR | SAV | 2025 | 6/1/2025
214 | 20466 | SMART VALVE INSTALLATION | GPC | 2025 | 6/1/2025
218 | 21046 | THALMANN AND COLERAIN 23O KV LINE RELAY PANEL UPGRADES | GPC | 2025 | 6/1/2025
211 | 20431 | VILLA RICA LOW SIDE BREAKER | GPC | 2025 | 6/1/2025
218 | 20684 | CAMDEN INDUSTRIAL PARK (GPC) | GPC | 2025 | 6/1/2025
213 | 18774 | GTC: HEARD COUNTY - TENASKA 500KV (SECOND LINE) | GTC | 2025 | 12/1/2025
206 | 18889 | JEFFERSON STREET#3 - NORTHWEST (WHITE) 115 KV RECONDUCTOR | GPC | 2025 | 12/1/2025
212 | 20326 | ANTHONY SHOALS STATCOM SYSTEM | GPC | 2025 | 12/31/2025
211 | 20152 | CC - CASS PINE- HILL VIEW 230 KV LINE- CC IMPROVEMENTS | GPC | 2025 | 12/31/2025
211 | 20175 | CC - PROJECT CHRONOS- SK/HYUNDAI | GPC | 2025 | 12/31/2025
215 | 20010 | GTC: ANTHONY SHOALS - WASHINGTON 115 KV LINE REBUILD | GTC | 2025 | 12/31/2025
219 | 17075 | SAV: LITTLE OGEECHEE 230- 115KV: RELAY MODERNIZATION | SAV | 2025 | 12/31/2025
216 | 18691 | GTC: LIZARD LOPE - WESTOVER 115 KV NEW LINE | GTC | 2026 | 3/1/2026
208 | 20018 | CC - QTS FAYETTEVILLE TRANSMISSION NEEDS | GPC | 2026 | 4/1/2026
208 | 19597 | ADAMSVILLE - BUZZARD ROOST 230KV REBUILD AND JUMPER UPGRADE | GPC | 2026 | 6/1/2026
201 | 18960 | BLANKETS CREEK – WOODSTOCK 115KV LINE REBUILD | GPC | 2026 | 6/1/2026
201 | 20243 | CC - GARRETT ROAD SWITCHING STATION - TRAE LANE | GPC | 2026 | 6/1/2026
208 | 20216 | CC - STONEWALL TELL ROAD (TA REALTY) | GPC | 2026 | 6/1/2026
211 | 18679 | DU: EAST DALTON - OOSTANAULA 115KV REBUILD | DU | 2026 | 6/1/2026
208 | 20491 | EAST POINT RELAY MODERNIZATION | GPC | 2026 | 6/1/2026
215 | 16007 | FENWICK STREET - SAND BAR FERRY 115KV (RECONDUCTOR/REBUILD) | GPC | 2026 | 6/1/2026
213 | 20516 | GOAT ROCK 230KV SWITCH, JUMPER, & LINE TRAP REPLACEMENT | GPC | 2026 | 6/1/2026
214 | 19618 | GORDON-N DUBLIN 115KV (GORDON-ENGL MCI J) REBUILD | GPC | 2026 | 6/1/2026
206 | 21139 | GRADY - MORROW (WHITE) 115KV REBUILD | GPC | 2026 | 6/1/2026
206 | 20474 | GRADY 230/115KV RELAY MODERNIZATION | GPC | 2026 | 6/1/2026
212 | 19706 | GRID - GAINESVILLE #2 EQUIPMENT REPLACEMENT | GPC | 2026 | 6/1/2026
206 | 21137 | GTC: CONYERS - CORNISH MOUNTAIN 115KV LINE UPGRADE | GTC | 2026 | 6/1/2026
213 | 19334 | GTC: LAGRANGE - NORTH OPELIKA 230 KV | GTC | 2026 | 6/1/2026
212 | 20015 | GTC: MORNING HORNET 2ND 230/115 KV BANK & THUMBS UP 115KV TL | GTC | 2026 | 6/1/2026
214 | 19999 | GTC: ROBINS SPRING BUS REPLACEMENT | GTC | 2026 | 6/1/2026
214 | 20001 | GTC: ROBINS SPRING CAPACITOR BANK INSTALLATION | GTC | 2026 | 6/1/2026
211 | 19636 | HAMMOND - WEISS DAM 115KV LINE REBUILD | GPC | 2026 | 6/1/2026
214 | 20512 | KATHLEEN AREA IMPROVEMENTS | GPC | 2026 | 6/1/2026
206 | 20490 | KLONDIKE RELAY MODERNIZATION | GPC | 2026 | 6/1/2026
213 | 19598 | MEAG: DRESDEN - LAGRANGE PRIMARY 230KV UPGRADE & JUMPERS | MEAG | 2026 | 6/1/2026
215 | 20270 | MEAG: RAY PLACE RD - WASHINGTON #3 | MEAG | 2026 | 6/1/2026
215 | 20271 | MEAG: RAY PLACE RD - WASHINGTON (WASHINGTON - WASHINGTON 3) | MEAG | 2026 | 6/1/2026
208 | 20300 | MORROW 115KV RELAY UPGRADE | GPC | 2026 | 6/1/2026
216 | 18690 | PALMYRA REACTOR REMOVAL | GPC | 2026 | 6/1/2026
219 | 20066 | SAV: BOULEVARD - DEPTFORD 115KV RECONDUCTOR | SAV | 2026 | 6/1/2026
219 | 19966 | SAV: CC - BIG OGEECHEE 500/230KV (CC NETWORK IMPROVEMENTS) | SAV | 2026 | 6/1/2026
219 | 20277 | SAV: MCINTOSH - PURRYSBURG 230KV REACTORS | SAV | 2026 | 6/1/2026
206 | 20489 | SCOTTDALE RELAY MODERNIZATION | GPC | 2026 | 6/1/2026
208 | 17900 | UNION CITY - YATES 230 KV WHITE LINE REBUILD | GPC | 2026 | 4/1/2026
208 | 20691 | UNION CITY - YATES 230KV (WHITE) SWITCH AND TRAP REPLACEMENT | GPC | 2026 | 6/1/2026
216 | 20223 | CC - PROJECT PAYTON BAINBRIDGE | GPC | 2026 | 6/30/2026
208 | 21022 | OHARA BREAKER REPLACEMENT | GPC | 2026 | 10/1/2026
208 | 20668 | DRESDEN LINE PROTECTIVE RELAYING | GPC | 2026 | 12/1/2026
213 | 20874 | GTC: BARNESVILLE PRIMARY- BARNESVILLE #1 115KV RECONDUCTOR | GTC | 2026 | 12/1/2026
208 | 20273 | GTC: DRESDEN 500KV BUS EXPANSION | GTC | 2026 | 12/1/2026
214 | 20002 | GTC: GORDON - SANDERSVILLE #1 115KV LINE REBUILD | GTC | 2026 | 12/1/2026
211 | 20151 | CC - CASS PINE 230/25 NEW SUB - QCELLS - CC IMPROVEMENTS | GPC | 2026 | 12/31/2026
206 | 19287 | GRADY-WEST END 115KV REBUILD | GPC | 2026 | 12/31/2026
208 | 19363 | MORROW - MOUNTAIN VIEW 115 KV REBUILD | GPC | 2026 | 12/31/2026
213 | 18832 | MEAG: FORTSON 230KV SUBSTATION MODERNIZATION | MEAG | 2027 | 1/13/2027
201 | 20509 | CC - EMBLEM RIVERSIDE CUSTOMER SUB (FLEXENTIAL) | GPC | 2027 | 3/1/2027
211 | 19635 | GTC: HICKORY LEVEL - VILLA RICA 230KV LINE RECONDUCTOR | GTC | 2027 | 5/1/2027
208 | 19601 | MORROW - YATES COMMON 115KV LINE UPGRADE | GPC | 2027 | 5/1/2027
211 | 15879 | POSSUM BRANCH - YATES COMMON 115KV REBUILD (YATES TO CLEM) | GPC | 2027 | 5/1/2027
208 | 20771 | CC - GULLATT ROAD TRANSMISSION IMPROVEMENTS | GPC | 2027 | 6/1/2027
208 | 18736 | CC - MICROSOFT - SHUGART (CCO06) | GPC | 2027 | 6/1/2027
201 | 20781 | CC - SUMMER LAKE - VILLA RICA 230KV REBUILD (CC IMPROVMNT) | GPC | 2027 | 6/1/2027
208 | 20736 | CC - TA REALTY ELLENWOOD NETWORK IMPROVEMENTS | GPC | 2027 | 6/1/2027
212 | 20234 | DOYLE - LG&E MONROE 230KV - JACKS CREEK LOOP IN | GPC | 2027 | 6/1/2027
201 | 20858 | GTC: ADAMSVILLE - BUZZARD ROOST 230KV REBUILD | GTC | 2027 | 6/1/2027
201 | 20776 | GTC: DOUGLASVILLE - VILLA RICA 230KV REBUILD (CC IMPROVEMENT) | GTC | 2027 | 6/1/2027
212 | 20778 | GTC: DOYLE - WINDER PRIMARY 230KV LINE JUMPER REPLACEMENT | GTC | 2027 | 6/1/2027
216 | 19358 | GTC: EAST MOULTRIE - HIGHWAY 112 230 KV LINE | GTC | 2027 | 6/1/2027
212 | 9662 | GTC: EAST WALTON 500/230KV PROJECT | GTC | 2027 | 6/1/2027
201 | 20505 | GTC: GARRETT RD - V. RICA 230KV LINE RECONDUCTOR (CC NET IM) | GTC | 2027 | 6/1/2027
214 | 19622 | GTC: RIDDLEVILLE BUS REPLACEMENT | GTC | 2027 | 6/1/2027
206 | 19606 | GTC: SKC 115KV BUS AND JUMPER REPLACEMENT | GTC | 2027 | 6/1/2027
214 | 20020 | GTC: SOUTH HAZLEHURST - NEW LACY 230KV LINE | GTC | 2027 | 6/1/2027
201 | 20506 | GTC: SWITCH WAY - THORNTON ROAD 230KV LINE REBUILD | GTC | 2027 | 6/1/2027
218 | 18668 | JESUP - OFFERMAN 115KV REBUILD | GPC | 2027 | 6/1/2027
202 | 10143 | LAWRENCEVILLE - WINDER 115KV LINE REBUILD | GPC | 2027 | 6/1/2027
202 | 10481 | LAWRENCEVILLE - WINDER PRIMARY 230KV LINE REBUILD | GPC | 2027 | 6/1/2027
215 | 20264 | MEAG: RAY PLACE RD - WARRENTON PRIMARY | MEAG | 2027 | 6/1/2027
214 | 19248 | SANDERSVILLE #1 - WADLEY PRI. 115KV REBUILD/RECONDUCTOR | GPC | 2027 | 6/1/2027
219 | 20785 | SAV: GOSHEN (SAV) - KRAFT 115KV LINE REBUILD | SAV | 2027 | 6/1/2027
219 | 20065 | SAV: GOSHEN (SAV) - MCINTOSH 115KV LINE REBUILD | SAV | 2027 | 6/1/2027
208 | 20717 | CC - TOMOCHICHI 500/230KV SOLUTION (CC NETWORK IMPROVEMENTS) | GPC | 2027 | 7/15/2027
214 | 18573 | GRID - ARKWRIGHT - LLOYD SHOALS 115KV | GPC | 2027 | 7/30/2027
214 | 20591 | GTC: EATONTON PRIMARY (035591) - LICK CREEK 115KV REBUILD | GTC | 2027 | 12/1/2027
212 | 17977 | ATHENA - EAST WATKINSVILLE 115 KV (REBUILD) | GPC | 2027 | 12/31/2027
211 | 20150 | CC - HILL VIEW & GRASSY HOLLOW SUB - CC IMPROVEMENTS | GPC | 2027 | 12/31/2027
211 | 20024 | DYER ROAD - EAST ROANOKE 115KV (REBUILD) | GPC | 2027 | 12/31/2027
214 | 19997 | AULTMAN ROAD-PERRY 115KV LINE REBUILD | GPC | 2028 | 6/1/2028
201 | 20797 | CC - EAST VILLA RICA AREA SWITCHING STATION (CC IMPROVEMENT) | GPC | 2028 | 6/1/2028
211 | 20774 | CC - VILLA RICA UPGRADES (CC NETWORK IMPROVEMENTS) | GPC | 2028 | 6/1/2028
214 | 21048 | FITZGERALD - PITTS 115 KV LINE REBUILD | GPC | 2028 | 6/1/2028
213 | 8458 | GTC: BARNESVILLE - SOUTH GRIFFIN 230KV PROJECT | GTC | 2028 | 6/1/2028
216 | 20503 | GTC: BARNEYVILLE - EAST MOULTRIE 115KV NEW LINE | GTC | 2028 | 6/1/2028
214 | 20873 | GTC: BONAIRE PRIMARY 500/230KV XFMR REPLCMNT & RELAY MOD | GTC | 2028 | 6/1/2028
212 | 19992 | GTC: BOSTWICK - EAST SOCIAL CIRCLE 230KV RECONDUCTOR | GTC | 2028 | 6/1/2028
206 | 20777 | JACK MCDONOUGH - NORTHWEST (BLACK) 230KV RECONDUCTOR | GPC | 2028 | 6/1/2028
216 | 19629 | MEAG: BRUMBLEY CREEK - SOUTH BAINBRIDGE 115KV REBUILD | MEAG | 2028 | 6/1/2028
216 | 19630 | MEAG: THOMASVILLE 230/115KV AUTOBANK REPLACEMENT | MEAG | 2028 | 6/1/2028
213 | 20482 | PITTMAN ROAD - WEST POINT DAM (USA) 115KV REBUILD | GPC | 2028 | 6/1/2028
208 | 20656 | PLANT YATES BREAKER AND HALF STATION | GPC | 2028 | 6/1/2028
219 | 20783 | SAV: COLEMAN - DEAN FOREST 115KV LINE REBUILD | SAV | 2028 | 6/1/2028
219 | 20407 | SAV: MAGNOLIA - TRUMAN PARKWAY 115KV REBUILD | SAV | 2028 | 6/1/2028
201 | 21069 | SMART VALVES AT EAST VILLA RICA SWITCHING STATION | GPC | 2028 | 6/1/2028
214 | 20768 | SOUTH MACON 115KV BUSES 1 & 2 REPLACEMENT | GPC | 2028 | 6/1/2028
208 | 20274 | UNION CITY - YATES 230KV (BLACK) LINE REBUILD | GPC | 2028 | 6/1/2028
213 | 13166 | FIRST AVENUE - NORTH COLUMBUS 115KV LINE REBUILD | GPC | 2028 | 12/1/2028
214 | 20586 | GTC: NORTH DUBLIN 230/115KV TRANSFORMERS AND BUS-TIE BREAKER | GTC | 2028 | 12/1/2028
208 | 21062 | ASHLEY PARK-WANSLEY 500KV | GPC | 2029 | 6/1/2029
216 | 10222 | BLAKELY PRIMARY - HUCKLEBERRY 115KV REBUILD | GPC | 2029 | 6/1/2029
214 | 21047 | BROADWAY - ECHECONNEE 115 KV LINE REBUILD | GPC | 2029 | 6/1/2029
213 | 16887 | BUTLER - THOMASTON 230KV LINE CONVERSION | GPC | 2029 | 6/1/2029
201 | 21036 | BUZZARD ROOST - FACTORY SHOALS 230KV NEW LINE | GPC | 2029 | 6/1/2029
206 | 21142 | CONYERS - KLONDIKE 230 KV SECOND LINE | GPC | 2029 | 6/1/2029
206 | 21138 | GLENWOOD SPRINGS - PORTERDALE PRIMARY 230KV LINE SWITCH REPL | GPC | 2029 | 6/1/2029
213 | 21112 | GTC: BARNESVILLE PRIMARY - THOMASTON 230KV | GTC | 2029 | 6/1/2029
202 | 10814 | GTC: BAY CREEK 230/115KV SECOND AUTO TRANSFORMER | GTC | 2029 | 6/1/2029
214 | 21140 | GTC: BONAIRE PRIMARY - EASTMAN PRIMARY 115 KV LINE REBUILD | GTC | 2029 | 6/1/2029
201 | 20849 | GTC: CLIFTONDALE - LINE CREEK 230KV LINE | GTC | 2029 | 6/1/2029
213 | 19950 | GTC: DRESDEN - TALBOT 500KV LINE | GTC | 2029 | 6/1/2029
202 | 20760 | GTC: HOPEWELL 230/115 KV BANK A | GTC | 2029 | 6/1/2029
201 | 21123 | GTC: TENASKA - WANSLEY 500KV NEW LINE | GTC | 2029 | 6/1/2029
206 | 21141 | LLOYD SHOALS - PORTERDALE PRIMARY 115KV REBUILD | GPC | 2029 | 6/1/2029
216 | 20285 | LOWER RIVER - WEBB (APC) 115KV RECONDUCTOR | GPC | 2029 | 6/1/2029
212 | 19621 | MCEVER ROAD - SHOAL CREEK 115KV REBUILD | GPC | 2029 | 6/1/2029
218 | 20346 | MCMANUS - WEST BRUNSWICK 115KV REBUILD | GPC | 2029 | 6/1/2029
214 | 17706 | MEAG: AULTMAN ROAD - FORT VALLEY #1 115 KV REBUILD | MEAG | 2029 | 6/1/2029
216 | 11051 | MEAG: SLAPPEY DRIVE - WESTOVER 115KV LINE REBUILD | MEAG | 2029 | 6/1/2029
202 | 20757 | NORCROSS - NORTH DRUID HILLS 115KV REBUILD | GPC | 2029 | 6/1/2029
219 | 21006 | SAV: BOULEVARD - MAGNOLIA 115 KV LINE REBUILD | SAV | 2029 | 6/1/2029
219 | 21023 | SAV: DEAN FOREST - LITTLE OGEECHEE 230 KV REBUILD | SAV | 2029 | 6/1/2029
219 | 20989 | SAV: RICE HOPE NEW AUTO TRANSFORMER | SAV | 2029 | 6/1/2029
216 | 13628 | SOUTH BAINBRIDGE - SINAI (FPL) 115KV LINE RECONDUCTOR | GPC | 2029 | 6/1/2029
202 | 20248 | BAY CREEK - CONYERS 230KV REBUILD | GPC | 2029 | 12/31/2029
211 | 21129 | ANNISTON - HAMMOND 230KV LINE | GPC | 2030 | 6/1/2030
201 | 20764 | ATKINSON - NORTHSIDE DRIVE 115KV REBUILD | GPC | 2030 | 6/1/2030
201 | 20761 | ATKINSON - NORTHWEST 115KV REBUILD | GPC | 2030 | 6/1/2030
212 | 21130 | CC - NORTH GEORGIA DATA NETWORK UPGRADES | GPC | 2030 | 6/1/2030
212 | 10478 | CORNELIA - TALLULAH LODGE 115KV REBUILD | GPC | 2030 | 6/1/2030
212 | 18669 | DU: DAWSON CROSSING - NELSON (WHITE) 115 KV REBUILD | DU | 2030 | 6/1/2030
201 | 21097 | EAST POINT - TRIBUTARY 230KV REBUILD | GPC | 2030 | 6/1/2030
208 | 20480 | EAST POINT - UNION CITY 230KV BLACK LINE RECONDUCTOR | GPC | 2030 | 6/1/2030
214 | 19627 | ECHECONNEE-WELLSTON 115KV LINE REBUILD | GPC | 2030 | 6/1/2030
216 | 21063 | FARLEY (APC)-TAZEWELL 500KV | GPC | 2030 | 6/1/2030
212 | 12120 | GAINESVILLE #2 - MCEVER ROAD 115 KV REBUILD | GPC | 2030 | 6/1/2030
214 | 20298 | GLENWOOD SPRINGS - LAKE OCONEE 115KV LINE REBUILD | GPC | 2030 | 6/1/2030
213 | 21128 | GOAT ROCK REACTORS INSTALLATION | GPC | 2030 | 6/1/2030
215 | 19996 | GOLDENS CREEK - WARRENTON PRIMARY 230KV REBUILD | GPC | 2030 | 6/1/2030
214 | 20428 | GORDON-SANDERSVILLE #1 115KV LINE REBUILD (DEEPSTEP-SAND #6) | GPC | 2030 | 6/1/2030
215 | 21116 | GOSHEN AREA STRATEGIC SOLUTION | GPC | 2030 | 6/1/2030
208 | 21073 | GTC: BIG SMARR - TOMOCHICHI 500KV | GTC | 2030 | 6/1/2030
201 | 21014 | GTC: BUZZARD ROOST - CAVENDER DRIVE 230KV NEW LINE | GTC | 2030 | 6/1/2030
201 | 21013 | GTC: CAVENDER DRIVE 500/230KV AUTOBANK | GTC | 2030 | 6/1/2030
212 | 20375 | GTC: EAST WATKINSVILLE 230 KV STATION MODIFICATION | GTC | 2030 | 6/1/2030
212 | 21111 | GTC: HARTWELL DAM - HARTWELL ENERGY 230KV SERIES REACTORS | GTC | 2030 | 6/1/2030
212 | 21113 | GTC: HARTWELL ENERGY - MIDDLE FORK 230KV LINE | GTC | 2030 | 6/1/2030
212 | 21131 | GTC: POND FORK - MIDWAY 115KV LINE | GTC | 2030 | 6/1/2030
214 | 21077 | GTC: ROCKVILLE - TIGER CREEK -WARTHEN 500KV LINES | GTC | 2030 | 6/1/2030
216 | 21076 | GTC: TALLBOT #2 - TAZEWELL 500KV LINE | GTC | 2030 | 6/1/2030
214 | 21094 | GTC: TIGER CREEK- ROCKVILLE-NORTH SPA 230KV PROJECT | GTC | 2030 | 6/1/2030
212 | 20789 | JEFFERSON ROAD - WINDER PRIMARY 115KV REBUILD | GPC | 2030 | 6/1/2030
216 | 20284 | KETTLE CREEK PRIMARY - PINE GROVE PRIMARY 115KV REBUILD | GPC | 2030 | 6/1/2030
215 | 21118 | MEAG: ATHENA - WARRENTON 230KV CONVERSION | MEAG | 2030 | 6/1/2030
201 | 20857 | NEW CAVENDER DRIVE - TRIBUTARY 230KV LINE | GPC | 2030 | 6/1/2030
214 | 21093 | NORTH SPA 230KV STRATEGIC PROJECT | GPC | 2030 | 6/1/2030
212 | 19995 | TALLULAH LODGE - TOCCOA 115 KV REBUILD | GPC | 2030 | 6/1/2030
201 | 21098 | TRIBUTARY - THORNTON RD 230KV REBUILD | GPC | 2030 | 6/1/2030
213 | 20160 | THOMASTON 230 NEW BUILD SUB | GPC | 2030 | 11/1/2030
216 | 18848 | BAINBRIDGE TRANSMISSION: EAST RIVER ROAD, EAST BAINBRIDGE | GPC | 2030 | 12/31/2030
214 | 19626 | GLENWOOD SPRINGS 115KV CAP BANK | GPC | 2030 | 12/31/2030
208 | 20690 | EAST POINT - UNION CITY (WHITE) 230KV REBUILD | GPC | 2031 | 5/1/2031
202 | 19632 | AVERY - HOPEWELL 115KV RECONDUCTOR | GPC | 2031 | 6/1/2031
211 | 10811 | BOWEN #10 500/230KV AUTOBANK REPLACEMENT | GPC | 2031 | 6/1/2031
215 | 20756 | HATCH - WADLEY 500 KV LINE STRATEGIC PROJECT | GPC | 2031 | 6/1/2031
214 | 21099 | MEAG: PIO NONO 230/115KV AREA SOLUTION | MEAG | 2031 | 6/1/2031
213 | 21114 | MEAG: SOUTH GRIFFIN 230/115KV BANK #5 | MEAG | 2032 | 6/1/2032
219 | 20784 | SAV: COLEMAN - MELDRIM 115KV LINE REBUILD | SAV | 2032 | 6/1/2032
214 | 20767 | ARKWRIGHT BUS AND JUMPER REPLACEMENT | GPC | 2033 | 6/1/2033
202 | 20758 | BAY CREEK - CONYERS 230KV LIMITING ELEMENT REPLACEMENT | GPC | 2033 | 6/1/2033
215 | 20793 | EVANS PRIMARY - THURMOND DAM (USA) #5 115KV REBUILD | GPC | 2033 | 6/1/2033
215 | 20794 | EVANS PRIMARY - THURMOND DAM (USA) #6 115KV REBUILD | GPC | 2033 | 6/1/2033
212 | 12217 | GTC: CENTER PRIMARY - CLARKSBORO 230 KV REBUILD | GTC | 2033 | 6/1/2033
212 | 20773 | GTC: CLARKSBORO - WINDER PRIMARY 230KV REBUILD | GTC | 2033 | 6/1/2033
212 | 12147 | GTC: EAST SOCIAL CIRCLE - SNELLVILLE 230KV EQUIPMENT UPGRADE | GTC | 2033 | 6/1/2033
212 | 21075 | GTC: EAST WALTON - MIDDLE FORK 500KV | GTC | 2033 | 6/1/2033
212 | 20791 | GTC: SHOAL CREEK - SOUTH HALL 230KV REBUILD | GTC | 2033 | 6/1/2033
212 | 21053 | MCEVER ROAD - SHOAL CREEK 115KV REBUILD PHASE III | GPC | 2033 | 6/1/2033
212 | 9661 | MCGRAU FORD - MIDDLE FORK 500KV LINE PROJECT | GPC | 2033 | 6/1/2033
219 | 20796 | SAV: MELDRIM BANK D REPLACEMENT | SAV | 2033 | 6/1/2033
215 | 14222 | THOMSON PRIMARY 230/115KV SECOND TRANSFORMER | GPC | 2033 | 6/1/2033
202 | 20759 | WINDER PRIMARY 230KV BUS 1-2 PARALLEL BUS-TIE INSTALLATION | GPC | 2033 | 6/1/2033
216 | 10487 | PINE GROVE PRIMARY - WEST VALDOSTA 115 KV RECONDUCTOR | GPC | 2033 | 12/31/2033
212 | 18700 | DAWSON CROSSING - GAINESVILLE #1 115 KV | GPC | 2034 | 6/1/2034
219 | 20787 | SAV: LITTLE OGEECHEE 230/115KV BANK REPLACEMENT | SAV | 2034 | 6/1/2034
215 | 17993 | EVANS PRIMARY - THOMSON PRIMARY 115KV REBUILD | GPC | 2034 | 12/31/2034

## DESC Geocoded
Project ID | Project Name / Endpoints (raw title) | Description | Need / Area Note | Status | Planned In-Service Date |  | matched_endpoint_1 | osm_name_1 | lat_1 | lon_1 | score_1 | matched_endpoint_2 | osm_name_2 | lat_2 | lon_2 | score_2 | center_lat | center_lon | confidence | match_method
6807 B | Queensboro - Ft Johnson 115 kV & Queensboro-Bayfront 115kV (Queensboro-James Island Sect) | Replace the Queensboro – Ft Johnson 115 kV Line and structures as they have reached the end of life. | This project is required due to address end of life issues. | In Progress | 12/31/23 | ['Queensboro', 'Ft Johnson', 'Bayfront'] | Ft Johnson | Marine Resources Center, Fort Johnson Estates, Charleston, Charleston County, South Carolina, 29412, United States | 32.7489 | -79.9014 | [6 empty] | 32.7489 | -79.9014 | LOW | NOMINATIM
0167C-D | Union Pier 115-13.8 kV Sub: Tap | Installing a 115 kV Tap to feed the future Union Pier 115 kV Sub. | This project is needed to for load growth in the Charleston area. | Planned | 12/31/27 | ['Union Pier'] | Union Pier | Union Pier Terminal, 32, Ansonborough, Charleston, Charleston County, South Carolina, 29401, United States | 32.7843 | -79.9256 | [6 empty] | 32.7843 | -79.9256 | LOW | NOMINATIM
0139 M,N | Okatie 230-115kV Substation, Jasper – Yemassee 230kV #1 Fold-in | Expand existing Okatie Transmission sub, add a 230-115 autobank and fold the Jasper – Yemassee 230 kV #1 line into the 230 kV side. Construct two additional 115 kV bus tie lines. | This project is needed to improve system performance and to meet NERC TPL and internal DESC Planning Criteria for reliability. | In Progress | 12/31/2024 | ['Okatie Jasper', 'Yemassee'] | Okatie Jasper | Okatie Park, Chelsea, Jasper County, South Carolina, United States | 32.3515 | -80.8853 |  | Yemassee | Yemassee, Hampton County, South Carolina, United States | 32.6902 | -80.8507 |  | 32.5209 | -80.868 | LOW | NOMINATIM
6341 A-F | Cainhoy - Hamlin 115kV: Rebuild Line and Cainhoy – Hamlin 115 kV #2: Construct New 115 kV Line | Upgrade the 954 ACSR portion of the Cainhoy – Hamlin 115 kV line to B795 ACSR conductor, construct a new Cainhoy – Hamlin 115 kV #2 line, add terminals to Cainhoy and Hamlin sub to accommodate upgrades. | This project is required due to load growth in the Mount Pleasant area and to meet NERC TPL and internal DESC Planning criteria. | In Progress | 12/01/25 | ['Cainhoy', 'Hamlin'] | Cainhoy | Cainhoy Substation | 32.9414 | -79.8423 | 80 | Hamlin | Hamlin Substation | 32.8599 | -79.7885 |  | 32.9007 | -79.8154 | MEDIUM | OVERPASS
6808 J | Eastover - Square D 115kV: Rebuild | Replace wooden H-Frame structures with Self Supporting Steel Structures and restring with 1272 ACSR conductor. | This project is required to address end of life and reliability issues on these lines. | In Progress | 06/01/24 | ['Eastover', 'Square D'] | Eastover | Eastover, Richland County, South Carolina, United States | 33.8771 | -80.6923 | [6 empty] | 33.8771 | -80.6923 | LOW | NOMINATIM
6808 K | Burton-St Helena 115kV: Rebuild Burton-Frogmore Transmission Section | Replace wooden structures with Self Supporting Steel Structures and restring with 1272 ACSR conductor for the Burton – Frogmore Transmission section. | This project is required to address end of life and reliability issues on these lines. | In Progress | 12/31/24 | ['Burton', 'St Helena', 'Frogmore Transmission'] | Burton | Burton, Beaufort County, South Carolina, United States | 32.4239 | -80.7459 |  | St Helena | Saint Helena Island, Beaufort County, South Carolina, 29920, United States | 32.3869 | -80.5607 |  | 32.4054 | -80.6533 | LOW | NOMINATIM
6808 L | Burton-St Helena 115kV: Frogmore Distribution - St Helena | Replace wooden structures with Self Supporting Steel Structures and upgrade to 795 ACSR for the Frogmore Distribution Tap – St. Helena section. | This project is required to address end of life and reliability issues on these lines. | In Progress | 12/31/25 | ['Burton', 'St Helena', 'Frogmore Distribution'] | Frogmore Distribution | Frogmore Substation | 32.3991 | -80.5711 | 75 | [5 empty] | 32.3991 | -80.5711 | MEDIUM | OVERPASS
6808 N,O | VCS1-Denny Terrace 230kV & VCS1-Pineland 230kV: Rebuild Single Circuit Sections | Replace wooden H-Frame structures with Self Supporting Steel Structures and restring with standard 1272 ACSR conductor. | This project is required to address end of life and reliability issues on these lines. | In Progress | 12/31/26 | ['VCS1', 'Denny Terrace', 'Pineland', 'Single Circuit Sections'] | Denny Terrace | Denny Terrace Substation | 34.0576 | -81.0616 | 80 | [5 empty] | 34.0576 | -81.0616 | MEDIUM | OVERPASS
6808 R | Wateree-Killian 230kV: Rebuild | Replace wooden H-Frame structures with Self Supporting Steel Structures. | This project is required to address end of life and reliability issues on these lines. | In Progress | 12/31/28 | ['Wateree', 'Killian'] | Wateree | Wateree Station | 33.8213 | -80.6284 | 80 | [5 empty] | 33.8213 | -80.6284 | MEDIUM | OVERPASS
6808 S | Okatie-Bluffton 115kV: Rebuild | Replace wooden H-Frame structures with Self Supporting Steel Structures and upgrade conductor to standard 1272 ACSR. | This project is required to address end of life and reliability issues on these lines. | In Progress | 06/01/2025 | ['Okatie', 'Bluffton'] | Bluffton | Bluffton Substation | 32.235 | -80.8534 | 80 | [5 empty] | 32.235 | -80.8534 | MEDIUM | OVERPASS
6808 U | Hopkins-CIP 230kV: Rebuild | Replace wooden H-Frame structures with Self Supporting Steel Structures. | This project is required to address end of life and reliability issues on these lines. | Planned | 12/31/25 | ['Hopkins', 'CIP'] | Hopkins | Hopkins, Richland County, South Carolina, 29061, United States | 33.9043 | -80.877 | [6 empty] | 33.9043 | -80.877 | LOW | NOMINATIM
6808 V | Faber Place-Bayfront 115kV: Rebuild North Bridge Terrace to Bayfront Section | Replace wooden structures with Self Supporting Steel Structures and upgrade conductor to standard 1272 ACSR. | This project is required to address end of life and reliability issues on these lines. | Planned | 12/31/28 | ['Faber Place', 'Bayfront', 'North Bridge Terrace to Bayfront'] | Faber Place | Faber Place, North Charleston, Charleston County, South Carolina, 29414, United States | 32.8463 | -80.0298 |  | Bayfront | Bayfront, James Island, Charleston County, South Carolina, 29412, United States | 32.7421 | -79.9634 |  | 32.7942 | -79.9966 | LOW | NOMINATIM
6808 W | Square D - Hopkins 115kV: Rebuild | Replace wooden H-Frame structures with Self Supporting Steel Structures and restring with 1272 ACSR conductor. | This project is required to address end of life and reliability issues on these lines. | In Progress | 9/30/2024 | ['Square D', 'Hopkins'] | Hopkins | Hopkins, Richland County, South Carolina, 29061, United States | 33.9043 | -80.877 | [6 empty] | 33.9043 | -80.877 | LOW | NOMINATIM
6809 E | Stevens Creek - Hooks 115kV/LR Plumb Branch 46kV Rebuilds | 9.5 miles. Scope includes rebuilding the 115 and 46 kV lines in this corridor SPDC. | This project is required to address end of life and reliability issues on these lines. | In Progress | 12/31/24 | ['Stevens Creek', 'Hooks /LR Plumb Branch Rebuilds'] | Stevens Creek | Stevens Creek Power Plant | 33.5626 | -82.0514 | 80 | [5 empty] | 33.5626 | -82.0514 | MEDIUM | OVERPASS
6809 G | Stevens Creek - Hooks 115kV/LR Plumb Branch 46kV | Upgrade 6.5 miles of aging conductor with 1272 ACSR and rebuild with SPDC. | This project is required to address end of life and reliability issues on these lines. | Planned | 12/31/25 | ['Stevens Creek', 'Hooks /LR Plumb Branch'] | Stevens Creek | Stevens Creek Power Plant | 33.5626 | -82.0514 | 80 | [5 empty] | 33.5626 | -82.0514 | MEDIUM | OVERPASS
6805 G | Edenwood Sub: #1 & #2 230-115kV Autobanks, Replace with 336MVA | Replace Autobank 1 and 2 at Edenwood Substation. | This project is required to address end of life and maintenance issues on these transformers. | In Progress | 12/25/24 | ['Edenwood', 'Autobanks 336MVA'] | Edenwood | Edenwood, Cayce, Lexington County, South Carolina, 29033, United States | 33.9538 | -81.0598 | [6 empty] | 33.9538 | -81.0598 | LOW | NOMINATIM
1060A, I, L | Williams St Sub: Replace Sw House & Relays, AM Williams Sub: Replace Sw House, and McMeekin Sub: Add Sw House | Replace switch house, switch house equipment, and relay panels at Williams Street substation. Replace the switch house at AM Williams substation. Add Switching House at McMeekin Substation to move relays from plant relay room. | This project is required to address end of life and maintenance issues on these transformers. | In Progress | 12/31/28 | ['Williams St', 'Sw House', 'Relays AM Williams', 'Sw House McMeekin'] | Williams St | Williams Street, The Vista, Columbia, Richland County, South Carolina, 29201, United States | 33.9995 | -81.0474 | [6 empty] | 33.9995 | -81.0474 | LOW | NOMINATIM
06005 B | Harleyville 115KV Transmission Tap – Construct (1.4 miles) | Extend the 115 kV line from the Blue Circle tap to the Harleyville substation to provide 115 kV service. | Load growth. | Planned | 3/31/2027 | ['Harleyville Transmission'] |  |  | 33.2241 | -80.4536 |  |  |  | 33.2099 | -80.4513 |  | 33.2099 | -80.4513 | HIGH | MANUAL
05004 P | Summerville: Replace and Spare 230-115kV 336MVA Auto Bank | Purchase a spare 230/115kV, 336MVA Autobank for the Southern Region to be stored at Summerville 230kV Sub. Include a pad, AC for heaters, and possibly a pit for oil containment. | Spare equipment needs. | In Progress | 12/31/2024 | ['Summerville', 'Spare 336MVA Auto'] | Summerville | Summerville, Dorchester County, South Carolina, United States | 33.0187 | -80.1763 | [6 empty] | 33.0187 | -80.1763 | LOW | NOMINATIM
06076A | Canadys-Ritter 115KV-Rebld SPDC 230/115KV 1272 (Approx 18 Miles) | Rebuild Canadys-Ritter 115 kV line as SPDC with 230 kV on one side and 115 kV on the other side. | This project is needed to improve system performance and to meet NERC TPL and internal DESC Planning Criteria for reliability. | In Progress | 6/1/2026 | ['Canadys', 'Ritter'] | Canadys | Canadys, Colleton County, South Carolina, 28474, United States | 33.0565 | -80.6197 |  | Ritter | Ritter, Colleton County, South Carolina, United States | 32.7896 | -80.6304 |  | 32.9231 | -80.625 | LOW | NOMINATIM
6359 | Yemassee– Ritter 230kV #1 & #2: Construct SPDC with B-1272 | Construct Ritter – Yemassee 230kV #1 and #2 SPDC with B1272 ACSR on both sides. Convert the existing Ritter – Yemassee 230 kV to 115 kV operation. Convert and add terminals at Ritter and Yemassee. Add 230 kV bus tie at Ritter and upgrade the Yemassee 230 kV bus tie. | This project is needed to improve system performance and to meet NERC TPL and internal DESC Planning Criteria for reliability. | Planned | 6/1/2026 | ['Yemassee', 'Ritter'] | Yemassee | Yemassee, Hampton County, South Carolina, United States | 32.6902 | -80.8507 |  | Ritter | Ritter, Colleton County, South Carolina, United States | 32.7896 | -80.6304 |  | 32.7399 | -80.7405 | LOW | NOMINATIM
06367 A - C, H | Riverport Tap: Construct Tap | Construct Okatie – Riverport 230 kV to feed new Distribution substation. | Load growth. | In Progress | 12/31/25 | ['Riverport'] | Riverport | Riverport Drive, Rivertown Row, Conway, Horry County, South Carolina, 29562, United States | 33.8579 | -79.0829 | [6 empty] | 33.8579 | -79.0829 | LOW | NOMINATIM
06367 D - G | Jasper – Okatie 230 kV #2: Construct | Construct a 230 kV line with B1272 ACSR from Jasper to Okatie 230/115kV Substation. The line is estimated to be 6.5 miles long. This makes Jasper a Medium Impact substation and will require a new CIP Hut. | This project is needed to improve system performance and to meet NERC TPL and internal DESC Planning Criteria for reliability. | In Progress | 12/31/25 | ['Jasper', 'Okatie'] | Jasper | Jasper Generating Plant | 32.3591 | -81.1246 | 80 | [5 empty] | 32.3591 | -81.1246 | MEDIUM | OVERPASS
06371 D | Wagener 115kV Tap: Construct Tap | Constructing a 115 kV Tap off the Edmund Switching Station- Owens Corning 115 kV Line to feed new Wagener Distribution substation. | Load growth. | Planned | 12/31/25 | ['Wagener'] | Wagener | Wagener, Aiken County, South Carolina, 19164, United States | 33.6524 | -81.3612 | [6 empty] | 33.6524 | -81.3612 | LOW | NOMINATIM
06372 A | Church Creek - Ritter 230kV - Replace 38 Large Angles and Dead Ends | Replace 6.5 miles of aging conductor. | Replacing approximately 38 guyed wooden structures due to recent failures in the fiberglass strain insulators along this line. Structures to be changed out are dead ends/large angles. | In Progress | 6/1/2024 | ['Church Creek', 'Ritter', 'Large Angles Dead Ends'] | Church Creek | Church Creek, Charleston, Charleston County, South Carolina, United States | 32.7091 | -80.1358 |  | Ritter | Ritter, Colleton County, South Carolina, United States | 32.7896 | -80.6304 |  | 32.7493 | -80.3831 | LOW | NOMINATIM
06810 F | VCS2-Ward 230kV: Rebuild Line | Rebuild 40 miles of 230 kV line. | This project is required to address end of life and maintenance issues. | Planned | 12/31/29 | ['VCS2', 'Ward'] | Ward | Howard Street | 33.9861 | -81.0057 | 80 | [5 empty] | 33.9861 | -81.0057 | MEDIUM | OVERPASS
06810 G | Goose Creek Reservoir: Rebuild Transmission Line Crossings | Rebuilding the Williams Goose Creek 230 and 115 kV lines and the Williams - Faber Place 230 kV line across the Goose Creek Reservoir. | This project is required to address end of life and maintenance issues. | In Progress | 12/31/24 | ['Goose Creek Reservoir', 'Transmission Crossings'] | Goose Creek Reservoir | Goose Creek Reservoir, Hanahan, Berkeley County, South Carolina, United States | 32.9533 | -80.0252 | [6 empty] | 32.9533 | -80.0252 | LOW | NOMINATIM
06810 H | Summerville 115kV Loop: Rebuild | Replacing several wood pole sections on the Summerville 115 kV Loop that have reached the end of life. | This project is required to address end of life and maintenance issues. | In Progress | 12/31/24 | ['Summerville Loop'] |  |  | 34.4719 | -85.3376 | [6 empty] | 34.4719 | -85.3376 | HIGH | MANUAL
6809 M | St George - Sumter 230kV Tie: Rebuild Line from Santee Substation - Duke/Progress Energy Tie | Rebuild Line from Santee Substation - Duke/Progress Energy Tie. | Grid hardening. | Planned | 12/31/2025 | ['St George', 'Sumter Tie', 'from Santee', 'Duke/Progress Energy Tie'] | St George | St. George, Dorchester County, South Carolina, 29477, United States | 33.186 | -80.5757 | [6 empty] | 33.186 | -80.5757 | LOW | NOMINATIM
5392 A-C | Coit – Gills Creek 115kV: Construct | Convert the existing Coit - Gills Creek 33 kV Line to 115 kV. Approximately 1.25 miles. Construct Gills Creek Terminal at Coit Bus #1. | Load growth. | In Progress | 12/31/2024 | ['Coit', 'Gills Creek'] | Coit | Coit Gas Turbine Peaking Plant, 300, Olympia, Columbia, Richland County, South Carolina, 29201, United States | 33.9802 | -81.0406 |  | Gills Creek | Gills Creek, Columbia, Richland County, South Carolina, 29209, United States | 33.9487 | -80.9876 |  | 33.9645 | -81.0141 | LOW | NOMINATIM
6810 A | Hooks - Thurmond 115kV Tie: Rebuild | Rebuilding section of line between Hooks and Thurmond. Approximately 2.3 miles. The line will be rebuilt on existing R/W using steel poles, 115 kV insulation, and 1272 ACSR conductor. | This project is required to address end of life and reliability issues on these lines. | In Progress | 12/31/2024 | ['Hooks', 'Thurmond Tie'] | Hooks | Hooks Pond, Horry County, South Carolina, United States | 34.1706 | -79.0914 | [6 empty] | 34.1706 | -79.0914 | LOW | NOMINATIM
6809 N | Batesburg - Saluda County 115kV: Rebuild | Rebuild 13.5 miles of conductor. | Grid hardening. | In Progress | 12/31/2025 | ['Batesburg', 'Saluda County'] | Batesburg | Batesburg, Batesburg-Leesville, Lexington County, South Carolina, 29060, United States | 33.9079 | -81.5473 |  | Saluda County | Saluda County, South Carolina, 29138, United States | 34.0008 | -81.7468 |  | 33.9544 | -81.6471 | LOW | NOMINATIM
6853 B-F | Scout 230 kV Sub and Fold-in: Construct | Construct 230kV Transmission Line for Scout Customer Substation and modify VCS1 and Killian terminals. | Load growth. | In Progress | 3/31/2026 | ['Scout'] | Scout | Scout Island, Port Royal, Beaufort County, South Carolina, 29905, United States | 32.3596 | -80.6976 | [6 empty] | 32.3596 | -80.6976 | LOW | NOMINATIM
6859 | Dawson 230kV Sub and Fold-in: Construct and Rebuild | Construct Dawson 230kV substation. Fold in the existing Canadys – Church Creek and Canadys – Faber Place 230kV lines at the Dawson 230kV substation (phase 1). Rebuild Canadys – Dawson 230kV #1 and #2 with B1272 ACSR (phase 2). | Load growth. | In Progress | 10/1/2025 (phase 1) and 10/1/2026 (phase 2) | ['Dawson'] | Dawson | Oliver C. Dawson Stadium, Naylor Street, Orangeburg, Orangeburg County, South Carolina, 29115, United States | 33.4986 | -80.8447 | [6 empty] | 33.4986 | -80.8447 | LOW | NOMINATIM
6852 | Urquhart – Toolebeck 115kV line: Rebuild | Upgrade the 477 ACSR portions of the Urquhart – Toolebeck 115 kV line to 1272 ACSR. Replace existing structures with Single Pole Double Circuit Structures. Approximately 12.5 miles. | This project is needed to improve system performance and to meet NERC TPL and internal DESC Planning Criteria for reliability. | In Progress | 8/12/2026 | ['Urquhart', 'Toolebeck'] | Urquhart | Urquhart Station | 33.4334 | -81.9092 | 80 | [5 empty] | 33.4334 | -81.9092 | MEDIUM | OVERPASS
6388 A | Williams-Summerville 230kV: Upgrade to SPDC B1272 ACSR | Rebuild the section of the Williams - Summerville 230 kV line from Ladson Jct to Williams. Line to upgraded to B-1272 and designed for a future second circuit. Approximately 10 miles. | This project is needed to improve system performance and to meet NERC TPL and internal DESC Planning Criteria for reliability. | Planned | 5/1/2027 | ['Williams', 'Summerville', 'to B1272'] | Williams | Williams, Colleton County, South Carolina, 29493, United States | 33.0346 | -80.8426 |  | Summerville | Summerville, Dorchester County, South Carolina, United States | 33.0187 | -80.1763 |  | 33.0266 | -80.5094 | LOW | NOMINATIM
0147 C, K | Cainhoy 115 kV Tap: Construct | Construct a 115 kV tap from Cainhoy to Clements Ferry. Approximately 2.8 miles. Construct terminal at Cainhoy. | Load growth. | Planned | 12/31/2027 | ['Cainhoy'] | Cainhoy | Cainhoy Substation | 32.9414 | -79.8423 | 80 | [5 empty] | 32.9414 | -79.8423 | MEDIUM | OVERPASS
0147 B, J | Jack Primus 115 kV Tap: Construct | Construct a 115 kV tap from Jack Primus to Clements Ferry. Approximately 2.2 miles. Construct terminals at Jack Primus. | Load growth. | Planned | 12/31/2027 | ['Jack Primus'] | Jack Primus | Jack Primus Road, Point Hope, Charleston, Berkeley County, South Carolina, 29492, United States | 32.9157 | -79.8863 | [6 empty] | 32.9157 | -79.8863 | LOW | NOMINATIM
6847 A-B, D-H | Church Creek – Faber Place – Charleston Transmission: Add 230kV Line | Construct a 230 kV transmission line from Church Creek to Charleston Transmission. The Church Creek – Faber Place 230kV and 115kV lines will be rebuilt, and a 230kV line will be added between Faber Place and Charleston Transmission. Add 230/115kV transformer at Charleston Transmission. Add/upgrade terminals and bus work at impacted substations. | This project is needed to improve system performance and to meet NERC TPL and internal DESC Planning Criteria for reliability. | In Progress | 05/01/2027 | ['Church Creek', 'Faber Place', 'Charleston Transmission', 'Add'] | Church Creek | Church Creek, Charleston, Charleston County, South Carolina, United States | 32.7091 | -80.1358 |  | Faber Place | Faber Place, North Charleston, Charleston County, South Carolina, 29414, United States | 32.8463 | -80.0298 |  | 32.7777 | -80.0828 | LOW | NOMINATIM
6846 A | Eastover – Sumter 115kV DEP Tie: Rebuild with 1272 ACSR | Upgrade the DESC section (approx. 1 mile) of the tie line from 397.5 ACSR Ibis to 1272 ACSR. | This project is needed to improve system performance and to meet NERC TPL and internal DESC Planning Criteria for reliability. | Planned | 05/31/2026 | ['Eastover', 'Sumter DEP Tie'] | Eastover | Eastover, Richland County, South Carolina, United States | 33.8771 | -80.6923 | [6 empty] | 33.8771 | -80.6923 | LOW | NOMINATIM
6810 U | Cameron Jct – Elloree 46 kV Rebuild | Rebuilding the Cameron Jct – Elloree 46 kV Line. 7.3 miles. | System hardening | Planned | 12/31/2026 | ['Cameron Jct', 'Elloree'] | Elloree | Elloree, Orangeburg County, South Carolina, United States | 33.531 | -80.572 | [6 empty] | 33.531 | -80.572 | LOW | NOMINATIM
6810 J | Elloree – Santee City 46 kV: Rebuild | Rebuilding the 46 kV line between Elloree and Santee City. 7 miles. | System hardening | Planned | 12/31/2027 | ['Elloree', 'Santee City'] | Elloree | Elloree, Orangeburg County, South Carolina, United States | 33.531 | -80.572 |  | Santee City | Santee Drive, Jasmine Lake, Garden City Beach, Horry County, South Carolina, 29576, United States | 33.5918 | -79.0204 |  | 33.5614 | -79.7962 | LOW | NOMINATIM
6810 O | Urquhart – Aiken PSA 46 kV: Rebuild | Rebuilding the section of 46 kV line from Urquhart to the Aiken PSA tap point. TBD if the scope of this project includes rebuilding the actual tap Aiken PSA. 4.5 miles. | System hardening | Planned | 12/31/2027 | ['Urquhart', 'Aiken PSA'] | Urquhart | Urquhart Station | 33.4334 | -81.9092 | 80 | [5 empty] | 33.4334 | -81.9092 | MEDIUM | OVERPASS
6810 T | Cameron Jct – Cameron – St Matthews 46 kV Rebuild | Rebuilding the 46 kV line between Cameron Jct and St Matthews. 9.8 miles. | System hardening. | Planned | 12/31/2028 | ['Cameron Jct', 'Cameron', 'St Matthews'] | Cameron | Cameron, Calhoun County, South Carolina, United States | 33.5577 | -80.7145 | [6 empty] | 33.5577 | -80.7145 | LOW | NOMINATIM

## GA ITS Geocoded
Zone | TEAMS Number | Project Name / Endpoints (raw title) | Sponsor (GPC/GTC/MEAG/DU/SAV) | Year Filed | Need / In-Service Date | endpoints_tried | matched_endpoint_1 | osm_name_1 | lat_1 | lon_1 | score_1 | matched_endpoint_2 | osm_name_2 | lat_2 | lon_2 | score_2 | center_lat | center_lon | confidence | match_method | Description
216 | 19631 | PINE GROVE PRIMARY 115 KV DUAL STAGE CAPACITOR BANK | GPC | 2025 | 6/1/2025 | ['PINE GROVE PRIMARY DUAL STAGE CAPACITOR'] |  | Pine Grove Primary Substation | 30.8817 | -83.228 | [6 empty] | 30.8819 | , -83.2281081 | HIGH | MANUAL | Install a Dual Stage 30MVAR capacitor bank at Pine Grove Primary.
219 | 20067 | SAV: DEPTFORD - MAGNOLIA 115KV RECONDUCTOR | SAV | 2025 | 6/1/2025 | ['DEPTFORD', 'MAGNOLIA'] | DEPTFORD | Deptford Substation | 32.0669 | -81.0484 | 80 |  | Magnolia Substation | 32.0227 | -81.0862 |  | 32.0448 | -81.0673 | MEDIUM | OVERPASS | Reconductor the Deptford - Magnolia 115kV line (approximately 5 miles) using 973.1 C7 ACCS (Everglades) conductor and upgrade the Deptford main bus.
214 | 20466 | SMART VALVE INSTALLATION | GPC | 2025 | 6/1/2025 | ['SMART VALVE INSTALLATION'] |  | Eatonton Substation | 33.3044 | -83.4028 | [6 empty] | 33.3044 | -83.4028 | MEDIUM | MANUAL | Installation of Smart Valve devices inside the Eatonton Primary substation on the Branch - Oasis 230kV and Eatonton Primary - Oasis 230kV lines.
218 | 21046 | THALMANN AND COLERAIN 23O KV LINE RELAY PANEL UPGRADES | GPC | 2025 | 6/1/2025 | ['THALMANN COLERAIN 23O UPGRADES'] |  | Thalmann Substation | 31.2939 | -81.6808 |  |  |  | 30.7955 | -81.6727 |  | 31.2939 | -81.6808 | HIGH | MANUAL | Relay protection modifications at GPC's Thalmann and Colerain substations to match relay scheme used at GTC's new Camden Industrial Park 230/115kV substation.
211 | 20431 | VILLA RICA LOW SIDE BREAKER | GPC | 2025 | 6/1/2025 | ['VILLA RICA LOW SIDE BREAKER'] |  | Villa Rica Substation | 33.7413 | -84.8555 | [6 empty] | 33.7413 | -84.8555 | HIGH | MANUAL | Replace a low side breaker at Villa Rica with a 4000A breaker.
218 | 20684 | CAMDEN INDUSTRIAL PARK (GPC) | GPC | 2025 | 6/1/2025 | ['CAMDEN INDUSTRIAL PARK'] |  |  | 34.2476 | -80.5946 |  |  |  | 30.7955 | -81.6727 |  | 34.2476 | -80.5946 | MEDIUM | MANUAL | This project will loop in GPC's existing Colerain to Thalman 230kV line into GTC's new Camden Industrial Park station. GPC's Kingsland termination at GTC's Kinlaw sub will be relocated to a new 115kV bay position.
213 | 18774 | GTC: HEARD COUNTY - TENASKA 500KV (SECOND LINE) | GTC | 2025 | 12/1/2025 | ['HEARD COUNTY', 'TENASKA'] | TENASKA | Tenaska Georgia Substation | 33.3516 | -84.9981 | 80 |  | Heard County Substation | 33.3587 | -84.9942 |  | 33.3516 | -84.9981 | HIGH | OVERPASS | GTC: Build a second Heard County - Tenaska 500kV line, 0.8 miles, with 100C (3) 1113 ACSR Bluejay conductors. Add a 500kV breaker at Heard County. GPC: Add a 500kV breaker at Tenaska.
206 | 18889 | JEFFERSON STREET#3 - NORTHWEST (WHITE) 115 KV RECONDUCTOR | GPC | 2025 | 12/1/2025 | ['JEFFERSON STREET#3', 'NORTHWEST'] | JEFFERSON STREET#3 | 3, Jefferson Street, Newnan, Coweta County, Georgia, 30263, United States | 33.3753 | -84.7994 |  | NORTHWEST | Coca-Cola USA Building, 310, North Avenue Northwest, Atlanta, Fulton County, Georgia, 30332, United States | 33.7704 | -84.3979 |  | 33.5729 | -84.5987 | LOW | NOMINATIM | Rebuild the 115kV White line from Northwest to Jefferson Street #3 (1.2 miles) with 200C 1351 ACSS conductor.
212 | 20326 | ANTHONY SHOALS STATCOM SYSTEM | GPC | 2025 | 12/31/2025 | ['ANTHONY SHOALS STATCOM SYSTEM'] |  | Anthony Shoals Substation | 34.0019 | -82.6363 | [6 empty] | 34.0019 | -82.6363 | HIGH | MANUAL | Install a + 150 / - 150 MVAR turnkey STATCOM system at Anthony Shoals 230kV substation.
211 | 20152 | CC - CASS PINE- HILL VIEW 230 KV LINE- CC IMPROVEMENTS | GPC | 2025 | 12/31/2025 | ['CASS PINE', 'HILL VIEW'] | HILL VIEW | View Hill Court, Sandy Springs, Fulton County, Georgia, 30350, United States | 33.9865 | -84.3548 | [6 empty] | 33.9865 | -84.3548 | LOW | NOMINATIM | Build a new 7.58 mile 200C 1351 ACSS conductor 230kV line between new Cass Pine and Hill View 230kV substations.
211 | 20175 | CC - PROJECT CHRONOS- SK/HYUNDAI | GPC | 2025 | 12/31/2025 | ['PROJECT CHRONOS', 'SK/HYUNDAI'] |  |  | 32.1667 | -81.4609 | [6 empty] | 32.1667 | -81.4609 | HIGH | MANUAL | GPC will build a 230/25kV station named Two Run Ranch and loop it into the Cartersville - Pinson 230kV line to serve SK Battery/Hyundai and new load in the area.
215 | 20010 | GTC: ANTHONY SHOALS - WASHINGTON 115 KV LINE REBUILD | GTC | 2025 | 12/31/2025 | ['ANTHONY SHOALS', 'WASHINGTON'] | ANTHONY SHOALS | Anthony Shoals Substation | 34.0018 | -82.6363 | 80 |  | Double Branches Road Substation | 33.7737 | -82.4026 |  | 33.8878 | -82.5193 | MEDIUM | OVERPASS | Rebuild 21 miles of the Double Branches Junction - Washington 115kV line section with 100C 795 ACSR conductor or higher rated conductor.
219 | 17075 | SAV: LITTLE OGEECHEE 230- 115KV: RELAY MODERNIZATION | SAV | 2025 | 12/31/2025 | ['LITTLE OGEECHEE'] | LITTLE OGEECHEE | Little Ogeechee Station | 32.0068 | -81.2532 | [6 empty] | 32.0068 | -81.2532 | HIGH | MANUAL | Relay modernization with conversion of the 230kV ring bus to BAAH topology and addition of BAAH rung for Big Ogeechee - Little Ogeechee (Red) 230kV Line. Rebuild 115kV straight bus to BAAH design.
216 | 18691 | GTC: LIZARD LOPE - WESTOVER 115 KV NEW LINE | GTC | 2026 | 3/1/2026 | ['LIZARD LOPE', 'WESTOVER'] | LIZARD LOPE | Lizard Lope Road, Calhoun County, Georgia, United States | 31.6139 | -84.5196 |  | WESTOVER | Westover, Albany, Dougherty County, Georgia, 31707, United States | 31.5893 | -84.2113 |  | 31.6016 | -84.3655 | LOW | NOMINATIM | Construct two new 115kV stations, Lizard Lope and Westover, and build a new 19.8 miles of 115kV line from Lizard Lope to Gillionville
208 | 20018 | CC - QTS FAYETTEVILLE TRANSMISSION NEEDS | GPC | 2026 | 4/1/2026 | ['QTS FAYETTEVILLE TRANSMISSION NEEDS'] |  | O'Hara Substation | 33.4819 | -84.3666 |  |  | Union Substation | 33.5534 | -84.5095 |  | 33.5177 | -84.438 | MEDIUM | MANUAL | Build a new 500/230kV substation (Ashley Park) splitting the Ohara - Union City 500kV line. Install two 500/230kV auto transformers at the Ashley Park station. At Ashley Park, the 500kV side will be a 4 - breaker ring bus, while the 230kV side will be a 2 - rung Breaker and a Half configuration. Build two new 230kV lines (~6 miles each) from Ashley Park to the high side of customer substations. The new lines will be built with bundled 200C 1351 ACSS Martin conductor.
208 | 19597 | ADAMSVILLE - BUZZARD ROOST 230KV REBUILD AND JUMPER UPGRADE | GPC | 2026 | 6/1/2026 | ['ADAMSVILLE', 'BUZZARD ROOST JUMPER'] | ADAMSVILLE | Adamsville, Atlanta, Fulton County, Georgia, 10331, United States | 33.7593 | -84.5052 | [6 empty] | 33.7593 | -84.5052 | LOW | NOMINATIM | Rebuild the line sections from Adamsville to Boat Rock Road (8.08 miles) on the Adamsville - Buzzard Roost 230kV line with 200C 1351 ACSS Martin conductor. Replace the AAC 750 jumper on the line at Adamsville with (2) 1590 AAC jumper. Replace 1590 AAC jumpers at Bakers Ferry and Boat Rock with (2) 1590 AAC jumpers. Replace 1600A line switches at Boat Rock with 3000A switches.
201 | 18960 | BLANKETS CREEK – WOODSTOCK 115KV LINE REBUILD | GPC | 2026 | 6/1/2026 | ['BLANKETS CREEK', 'WOODSTOCK'] | BLANKETS CREEK | Blankets Creek Substation | 34.1858 | -84.508 | 80 |  | Woodstock Substation | 34.0853 | -84.5134 |  | 34.1355 | -84.5107 | HIGH | OVERPASS | Rebuild the entire Blankets Creek - Woodstock 115kV line, approximately 7.1 miles, with 200C 795 ACSS conductor.
201 | 20243 | CC - GARRETT ROAD SWITCHING STATION - TRAE LANE | GPC | 2026 | 6/1/2026 | ['GARRETT ROAD SWITCHING STATION', 'TRAE LANE'] | TRAE LANE | Villa Rica Substation | 33.7411 | -84.8554 | [6 empty] | 33.7411 | -84.8554 | MEDIUM | MANUAL | Build the new Garrett Road 230kV switching station (three - element ring bus) splitting the Villa Rica - West Marietta 230kV line. Build a new 230kV line (8.6 miles) from the Trae Lane substation to the Garrett Road switching station with bundled 100C 1351 ACSR conductor.
208 | 20216 | CC - STONEWALL TELL ROAD (TA REALTY) | GPC | 2026 | 6/1/2026 | ['STONEWALL TELL ROAD'] | STONEWALL TELL ROAD | Eastpoint Primary Substation | 33.6763 | -84.4631 |  |  | Union Substation | 33.5536 | -84.5097 |  | 33.6149 | -84.4864 | MEDIUM | MANUAL | Build 230kV line segment, using 200C 1351 ACSS Martin conductor, to loop in the Stonewall Tell Road (TA Realty) customer station into the East Point - Union City 230kV Black line.
211 | 18679 | DU: EAST DALTON - OOSTANAULA 115KV REBUILD | DU | 2026 | 6/1/2026 | ['EAST DALTON', 'OOSTANAULA'] | EAST DALTON | East Mount Haven Drive, Dalton, Whitfield County, Georgia, 30722, United States | 34.7784 | -85.0039 |  | OOSTANAULA | Oostanaula, Gordon County, Georgia, 30703, United States | 34.4815 | -85.0144 |  | 34.6299 | -85.0092 | LOW | NOMINATIM | DU: Rebuild the portion of East Dalton - Oostanaula and Dalton - East Dalton 115kV double circuit lines between East Dalton substation and the Dalton substation frame with 200C 795 ACSS.
208 | 20491 | EAST POINT RELAY MODERNIZATION | GPC | 2026 | 6/1/2026 | ['EAST POINT'] | EAST POINT | East Point Primary Substation | 33.6763 | -84.463 | 80 | [5 empty] | 33.6763 | -84.463 | MEDIUM | OVERPASS | Upgrade protection on 230kV buses, 115kV buses, and 230/115kV auto transformer at the East Point station. Add adequate monitoring on DC supply.
215 | 16007 | FENWICK STREET - SAND BAR FERRY 115KV (RECONDUCTOR/REBUILD) | GPC | 2026 | 6/1/2026 | ['FENWICK STREET', 'SAND BAR FERRY'] | FENWICK STREET | Fenwick Street, Augusta, Richmond County, Georgia, 30901, United States | 33.4687 | -81.9665 |  | SAND BAR FERRY | Sand Bar Ferry Road, Marion Homes, Augusta, Richmond County, Georgia, 30901, United States | 33.4486 | -81.9226 |  | 33.4586 | -81.9445 | LOW | NOMINATIM | Reconductor approximately 2.72 miles of transmission line from Fenwick St to East Augusta Jct. with 100C 1351 ACSR conductor.
213 | 20516 | GOAT ROCK 230KV SWITCH, JUMPER, & LINE TRAP REPLACEMENT | GPC | 2026 | 6/1/2026 | ['GOAT ROCK SWITCH JUMPER', 'TRAP REPLACEMENT'] |  |  | 32.6083 | -85.0824 | [6 empty] | 32.6083 | -85.0824 | HIGH | MANUAL | Replace the 230kV 1200A switch with 3000A, 90C 1351.5 ACSR Martin jumper with (2) AAC 1590, and 1600A line trap with 3000A (part of the Goat Rock - North Opelika 230kV line at Goat Rock substation.
214 | 19618 | GORDON-N DUBLIN 115KV (GORDON-ENGL MCI J) REBUILD | GPC | 2026 | 6/1/2026 | ['GORDON', 'N DUBLIN'] | GORDON | Gordon County, Georgia, United States | 34.502 | -84.8986 |  | N DUBLIN | Dublin, Laurens County, Georgia, United States | 32.5404 | -82.9038 |  | 33.5212 | -83.9012 | LOW | NOMINATIM | Rebuild the Gordon - Engelhard McIntyre J of the Gordon - North Dublin 115kV line from 100C 336.4 ACSR (2.81 miles) Linnet and 75C 4/0 F Copper/CW (3.18 miles) to 200C ACSS 795 conductor.
206 | 21139 | GRADY - MORROW (WHITE) 115KV REBUILD | GPC | 2026 | 6/1/2026 | ['GRADY', 'MORROW'] | MORROW | Morrow Substation | 33.6059 | -84.3335 | 80 | [5 empty] | 33.6059 | -84.3335 | MEDIUM | OVERPASS | Replace 0.72 miles of conductor from Moreland Way to Morrow including the bus and jumper at Moreland Way with 1351.5 Martin/ACSS 54/19 conductor.
206 | 20474 | GRADY 230/115KV RELAY MODERNIZATION | GPC | 2026 | 6/1/2026 | ['GRADY'] | GRADY | Grady County, Georgia, United States | 30.8671 | -84.2323 | [6 empty] | 30.8671 | -84.2323 | LOW | NOMINATIM | Upgrade protection on 230kV bus, all 115kV buses, and both 230/115kV auto transformers at Grady. Add adequate monitoring on DC supply. Install a 230kV breaker and associated switches on the high side of Grady 230/115kV auto transformer D.
212 | 19706 | GRID - GAINESVILLE #2 EQUIPMENT REPLACEMENT | GPC | 2026 | 6/1/2026 | ['GRID', 'GAINESVILLE EQUIPMENT REPLACEMENT'] | GRID | Gainesville Substation #2 | 34.263 | -83.8097 | [6 empty] | 34.263 | -83.8097 | HIGH | MANUAL | GPC: Replace the two 230/115kV auto transformers (Bank C and D) at Gainesville #2 with 400MVA. Project was originally maintenance driven but now compliance driven.
206 | 21137 | GTC: CONYERS - CORNISH MOUNTAIN 115KV LINE UPGRADE | GTC | 2026 | 6/1/2026 | ['CONYERS', 'CORNISH MOUNTAIN'] | CONYERS | Conyers, Rockdale County, Georgia, United States | 33.6676 | -84.0177 |  | CORNISH MOUNTAIN | Cornish Mountain, Newton County, Georgia, 30053, United States | 33.6734 | -83.8138 |  | 33.6705 | -83.9157 | LOW | NOMINATIM | Upgrade 750 jumpers at North Conyers and raise the temperature rating of the 636 ACSR conductor on the Conyers - Cornish MTN 115kV line from 100C to 125C.
213 | 19334 | GTC: LAGRANGE - NORTH OPELIKA 230 KV | GTC | 2026 | 6/1/2026 | ['LAGRANGE', 'NORTH OPELIKA'] | LAGRANGE | LaGrange Primary Substation | 33.0241 | -85.0157 | [6 empty] | 33.0241 | -85.0157 | MEDIUM | NOMINATIM | Build a new Lagrange - North Opelika (APC) 230kV line, 29.4 miles, with 100C ACSR 1351.5 Martin Conductor. GTC will construct the ~15 - mile section from Lagrange to the Metering Station near the Georgia - Alabama border. The Metering Station will be owned by GTC. GPC will construct the short line section from the Metering Station to the GA - AL state line. APC will construct the 230kV line from the GA - AL state line to North Opelika.
212 | 20015 | GTC: MORNING HORNET 2ND 230/115 KV BANK & THUMBS UP 115KV TL | GTC | 2026 | 6/1/2026 | ['MORNING HORNET 2ND', 'THUMBS UP TL'] |  | East Social Circle Station | 33.6741 | -83.6794 |  |  | Social Circle Primary Substation | 33.6814 | -83.7038 |  | 33.6777 | -83.6916 | LOW | MANUAL | GTC to add a second 230/115kV auto transformer at Morning Hornet substation. Also, build an additional 115kV line from Morning Hornet to Thumbs Up, approximately 2.4 miles, using at least 100C 1351 ACSR conductor.
214 | 19999 | GTC: ROBINS SPRING BUS REPLACEMENT | GTC | 2026 | 6/1/2026 | ['ROBINS SPRING REPLACEMENT'] |  | Robins Spring Substation | 33.0055 | -82.8798 | [6 empty] | 33.0055 | -82.8798 | HIGH | MANUAL | GTC: Replace the main 115kV bus 90C ACSR 336.4 Linnet conductor with higher rating.
214 | 20001 | GTC: ROBINS SPRING CAPACITOR BANK INSTALLATION | GTC | 2026 | 6/1/2026 | ['ROBINS SPRING CAPACITOR INSTALLATION'] |  | Robins Spring Substation | 33.0055 | -82.8798 | [6 empty] | 33.0055 | -82.8798 | HIGH | MANUAL | Install a 115kV 2 - stage 22.5MVAR (45MVAR total) capacitor bank at Robins Spring
211 | 19636 | HAMMOND - WEISS DAM 115KV LINE REBUILD | GPC | 2026 | 6/1/2026 | ['HAMMOND', 'WEISS DAM'] | HAMMOND | Hammond, Sandy Springs, Fulton County, Georgia, 30328, United States | 33.9254 | -84.3674 | [6 empty] | 33.9254 | -84.3674 | LOW | NOMINATIM | Rebuild 11.2 miles of Hammond - Weiss Dam 115kV from Hammond to the APC border with 200C 795 ACSS.
214 | 20512 | KATHLEEN AREA IMPROVEMENTS | GPC | 2026 | 6/1/2026 | ['KATHLEEN AREA'] |  | Bonaire Primary Substation | 32.5653 | -83.5998 | [6 empty] | 32.5653 | -83.5998 | MEDIUM | MANUAL | Rebuild the Kathleen - Big Grocery Creek 230kV line (approximately 1.5 miles). Rebuild the Bonaire Primary - Kathleen 230kV line (approximately 6 miles). Upgrade limiting elements at Kathleen substation.
206 | 20490 | KLONDIKE RELAY MODERNIZATION | GPC | 2026 | 6/1/2026 | ['KLONDIKE'] | KLONDIKE | Klondike Substation | 33.6369 | -84.1245 | [6 empty] | 33.6369 | -84.1245 | HIGH | MANUAL | Upgrade protection on 230kV buses at the Klondike station. Add adequate monitoring on DC supply.
213 | 19598 | MEAG: DRESDEN - LAGRANGE PRIMARY 230KV UPGRADE & JUMPERS | MEAG | 2026 | 6/1/2026 | ['DRESDEN', 'LAGRANGE PRIMARY', 'JUMPERS'] | LAGRANGE PRIMARY | LaGrange Primary Substation | 33.0241 | -85.0157 | 80 |  | Dresden Substation | 33.3513 | -84.9058 |  | 33.1877 | -84.9609 | MEDIUM | OVERPASS | MEAG will re-sag the Dresden - LaGrange Primary 230kV line to 125C. Replace the jumpers at Dresden and LaGrange with (2) 1590 AAC jumpers.
215 | 20270 | MEAG: RAY PLACE RD - WASHINGTON #3 | MEAG | 2026 | 6/1/2026 | ['RAY PLACE RD', 'WASHINGTON'] | RAY PLACE RD | Ray Place Road, Warren County, Georgia, United States | 33.4617 | -82.8297 |  | WASHINGTON | Washington County, Georgia, United States | 32.962 | -82.7748 |  | 33.2119 | -82.8023 | LOW | NOMINATIM | Rebuild the Ray Place Rd - Washington 115kV line with 100C 795 ACSR conductor (total 17.4 Miles) between Ray Place Rd and Washington 2. Replace Jumpers and bus at Washington 2.
215 | 20271 | MEAG: RAY PLACE RD - WASHINGTON (WASHINGTON - WASHINGTON 3) | MEAG | 2026 | 6/1/2026 | ['RAY PLACE RD', 'WASHINGTON'] | RAY PLACE RD | Ray Place Road, Warren County, Georgia, United States | 33.4617 | -82.8297 |  | WASHINGTON | Washington County, Georgia, United States | 32.962 | -82.7748 |  | 33.2119 | -82.8023 | LOW | NOMINATIM | MEAG will rebuild the Ray Place Rd - Washington 115kV line with 100C 1351 ACSR conductor (total 1.2 Miles) between Washington and Washington 3. Replace jumpers at Washington.
208 | 20300 | MORROW 115KV RELAY UPGRADE | GPC | 2026 | 6/1/2026 | ['MORROW'] | MORROW | Morrow Substation | 33.6059 | -84.3335 | 80 | [5 empty] | 33.6059 | -84.3335 | HIGH | OVERPASS | Upgrade protection scheme on all three 115kV buses at Morrow.
216 | 18690 | PALMYRA REACTOR REMOVAL | GPC | 2026 | 6/1/2026 | ['PALMYRA REACTOR REMOVAL'] |  |  | 39.8363 | -91.5512 | [6 empty] | 39.8363 | -91.5512 | MEDIUM | MANUAL | Remove the 6% reactor at the Palmyra Substation.
219 | 20066 | SAV: BOULEVARD - DEPTFORD 115KV RECONDUCTOR | SAV | 2026 | 6/1/2026 | ['BOULEVARD', 'DEPTFORD'] | BOULEVARD | Boulevard Substation | 32.0412 | -81.1445 | 80 | DEPTFORD | Deptford Substation | 32.0668 | -81.0484 | 80 | 32.054 | -81.0964 | MEDIUM | OVERPASS | Reconductor the Boulevard - Deptford 115kV line (approximately 8 miles) using 973.1 C7 ACCS (Everglades) conductor. Upgrade main bus and jumpers at Bolton substation from 90C 1590 AAC Coreopsis to 90C (2)1590 AAC Coreopsis or higher rated equipment.
219 | 19966 | SAV: CC - BIG OGEECHEE 500/230KV (CC NETWORK IMPROVEMENTS) | SAV | 2026 | 6/1/2026 | ['BIG OGEECHEE'] |  |  | 32.007 | -81.2531 | [6 empty] | 32.007 | -81.2531 | MEDIUM | MANUAL | Construct a new substation near Little Ogeechee, adjacent to the 500kV and 230kV shared right of way for McCall Road - Thalmann 500kV and the Little Ogeechee - Meldrim 230kV Black and White lines. The new substation will loop in the existing McCall Road - Thalmann 500kV line, the existing Little Ogeechee - Meldrim 230kV lines, and accommodate a new 1344MVA 500/230kV auto transformers with an additional 230kV connection to Little Ogeechee.
219 | 20277 | SAV: MCINTOSH - PURRYSBURG 230KV REACTORS | SAV | 2026 | 6/1/2026 | ['MCINTOSH', 'PURRYSBURG REACTORS'] | MCINTOSH | McIntosh County, Georgia, United States | 31.498 | -81.3922 | [6 empty] | 31.498 | -81.3922 | LOW | NOMINATIM | Install reactors on the McIntosh - Purrysburg (Black and White) 230kV tie lines at McIntosh. Rebuild 0.1 miles (GPC portion) for both lines to (2) 200C 1351 ACSS conductor.
206 | 20489 | SCOTTDALE RELAY MODERNIZATION | GPC | 2026 | 6/1/2026 | ['SCOTTDALE'] | SCOTTDALE | Scottdale, Clarkston, DeKalb County, Georgia, 30079, United States | 33.7971 | -84.2699 | [6 empty] | 33.7971 | -84.2699 | LOW | NOMINATIM | Upgrade protection on 230kV bus and 230/115kV auto transformers at the Scottdale station. Add adequate monitoring on DC supply.
208 | 17900 | UNION CITY - YATES 230 KV WHITE LINE REBUILD | GPC | 2026 | 4/1/2026 | ['UNION CITY', 'YATES WHITE'] | UNION CITY | Union Substation | 33.5536 | -84.5097 |  |  | Plant Yates | 33.4534 | -84.9055 |  | 33.5036 | -84.7077 | HIGH | MANUAL | Rebuild 23.4 miles of the Union City - Yates 230kV White line with bundled 1351 ACSS Martin conductor at 200C.
208 | 20691 | UNION CITY - YATES 230KV (WHITE) SWITCH AND TRAP REPLACEMENT | GPC | 2026 | 6/1/2026 | ['UNION CITY', 'YATES SWITCH TRAP REPLACEMENT'] | UNION CITY | Union Substation | 33.5536 | -84.5097 |  |  | Plant Yates | 33.4534 | -84.9055 |  | 33.5036 | -84.7077 | HIGH | MANUAL | Replace the limiting elements at Union City and Yates substations along the Union City - Yates 230kV (White) line.
216 | 20223 | CC - PROJECT PAYTON BAINBRIDGE | GPC | 2026 | 6/30/2026 | ['PROJECT PAYTON BAINBRIDGE'] |  | South Bainbridge Substation | 30.8396 | -84.4889 |  |  | Farley Substation | 31.2237 | -85.1161 |  | 31.0321 | -84.8019 | HIGH | MANUAL | Split Farley - South Bainbridge 230kV line with a 230kV station (Dothan Road) and bring an 8.5 mile 200C 1351 ACSS 230kV line from Dothan Rd to new customer sub Downrange. Bring another 10mile 200C 1351 ACSS 230kV line from Climax to customer sub Downrange.
208 | 21022 | OHARA BREAKER REPLACEMENT | GPC | 2026 | 10/1/2026 | ['OHARA BREAKER REPLACEMENT'] |  | O'Hara Substation | 33.4819 | -84.3666 |  |  | Tara Substation | 33.5275 | -84.4228 |  | 33.5047 | -84.3947 | HIGH | MANUAL | Replace Breaker on the Ohara - Tara 115kV Line at the Ohara Substation.
208 | 20668 | DRESDEN LINE PROTECTIVE RELAYING | GPC | 2026 | 12/1/2026 | ['DRESDEN PROTECTIVE RELAYING'] |  | O'Hara Substation | 33.4819 | -84.3666 |  |  | Wansley Substation | 33.4109 | -85.0308 |  | 33.4469 | -84.6988 | HIGH | MANUAL | On the O'Hara - Wansley 500kV line, replace the protective relay panels associated with the 500kV line terminal facing Dresden, at both O'Hara and Wansley.
213 | 20874 | GTC: BARNESVILLE PRIMARY- BARNESVILLE #1 115KV RECONDUCTOR | GTC | 2026 | 12/1/2026 | ['BARNESVILLE PRIMARY', 'BARNESVILLE'] | BARNESVILLE PRIMARY | Barnesville Primary Substation | 33.0321 | -84.2013 | 80 |  | Barnesville Substation #1 | 33.0555 | -84.153 |  | 33.0438 | -84.1771 | MEDIUM | OVERPASS | Rebuild approximately 4.53 miles of the Barnesville Primary - Barnesville #1 segment on the Barnesville Primary - Lamar County Industrial 115kV line.
208 | 20273 | GTC: DRESDEN 500KV BUS EXPANSION | GTC | 2026 | 12/1/2026 | ['DRESDEN EXPANSION'] |  | Dresden Substation | 33.3513 | -84.9058 | [6 empty] | 33.3513 | -84.9058 | HIGH | MANUAL | GTC will expand the Dresden 500kV bus into a 5 - element ring bus configuration. Loop the O'Hara - Wansley 500kV line into the Dresden 500kV substation and allow for future Dresden - Talbot 500kV line termination.
214 | 20002 | GTC: GORDON - SANDERSVILLE #1 115KV LINE REBUILD | GTC | 2026 | 12/1/2026 | ['GORDON', 'SANDERSVILLE'] | SANDERSVILLE | Sandersville Substation #1 | 32.9985 | -82.8019 | 80 |  | Sandersville Substation #6 | 33.0018 | -82.8327 |  | 33.0001 | -82.8173 | HIGH | OVERPASS | Rebuild the 1.87 miles of Sandersville #1 - Sandersville #6 line section of the Gordon - Sandersville #1 115kV line from 100C ACSR 336 conductor to 100C ACSR 795 conductor.
211 | 20151 | CC - CASS PINE 230/25 NEW SUB - QCELLS - CC IMPROVEMENTS | GPC | 2026 | 12/31/2026 | ['CASS PINE 230/25', 'QCELLS'] | QCELLS | Hanwha QCells, Cartersville, Bartow County, Georgia, United States | 34.2873 | -84.7917 | [6 empty] | 34.2873 | -84.7917 | LOW | NOMINATIM | Build a new 230/25kV 8 element ring bus networked substation named Cass Pine that will interconnect between new Great Valley and Hill View 230kV substations.
206 | 19287 | GRADY-WEST END 115KV REBUILD | GPC | 2026 | 12/31/2026 | ['GRADY', 'WEST END'] | GRADY | Grady County, Georgia, United States | 30.8671 | -84.2323 |  | WEST END | West End, 680, Lee Street Southwest, West End, Atlanta, Fulton County, Georgia, 30310, United States | 33.7361 | -84.4137 |  | 32.3016 | -84.323 | LOW | NOMINATIM | Reconductor the Grady - West End 115kV line (2.6 miles) using 200C 1351 ACSS Martin.
208 | 19363 | MORROW - MOUNTAIN VIEW 115 KV REBUILD | GPC | 2026 | 12/31/2026 | ['MORROW', 'MOUNTAIN VIEW'] | MORROW | Morrow Substation | 33.6059 | -84.3335 | 80 | [5 empty] | 33.6059 | -84.3335 | MEDIUM | OVERPASS | Rebuild the Mountain View - Barnett Road section of the Morrow - Mountain View 115kV line with 200C 1351 ACSS Martin conductor.
213 | 18832 | MEAG: FORTSON 230KV SUBSTATION MODERNIZATION | MEAG | 2027 | 1/13/2027 | ['FORTSON'] | FORTSON | Fortson, Hampton, Henry County, Georgia, 30284, United States | 33.3779 | -84.2888 | [6 empty] | 33.3779 | -84.2888 | LOW | NOMINATIM | Complete modernization and replacement of obsolete equipment and relays for the 500kV, 230kV, and 115kV yards. Add a redundant relay scheme at Fortson.
201 | 20509 | CC - EMBLEM RIVERSIDE CUSTOMER SUB (FLEXENTIAL) | GPC | 2027 | 3/1/2027 | ['EMBLEM RIVERSIDE CUSTOMER'] |  |  | 38.1917 | -82.6045 | [6 empty] | 38.1917 | -82.6045 | MEDIUM | MANUAL | A new customer substation, Emblem Riverside, is being built along the Buzzard Roost - Douglasville 230kV line. Moreover, a Fiber ICON ring is being built in the area to help with communications and protection for all customers in the area.
211 | 19635 | GTC: HICKORY LEVEL - VILLA RICA 230KV LINE RECONDUCTOR | GTC | 2027 | 5/1/2027 | ['HICKORY LEVEL', 'VILLA RICA'] | HICKORY LEVEL | Hickory Level Creek, Banks County, Georgia, United States | 34.2798 | -83.4991 |  | VILLA RICA | Villa Rica, Carroll County, Georgia, 30180, United States | 33.7321 | -84.9191 |  | 34.0059 | -84.2091 | LOW | NOMINATIM | GTC will reconductor from 100C 1351 ACSR to 160C 1351 ACSS on 8.6 miles of 230kV line. A 2000A line trap at Villa Rica will also be replaced with a 3000A line trap.
208 | 19601 | MORROW - YATES COMMON 115KV LINE UPGRADE | GPC | 2027 | 5/1/2027 | ['MORROW', 'YATES COMMON'] | MORROW | Morrow Substation | 33.6059 | -84.3335 | 80 | YATES COMMON | Yates Common Substation | 33.4616 | -84.9042 | 80 | 33.5338 | -84.6188 | MEDIUM | OVERPASS | On the Fife - Fairburn SW - Owens Corning Tap sections of the Morrow - Yates Common 115kV line, rebuild approximately 5.8 miles of 50C 477 ACSR with 210C 1334 T13 ACCR Martin or 200C 1351.0 ACSS Martin.
211 | 15879 | POSSUM BRANCH - YATES COMMON 115KV REBUILD (YATES TO CLEM) | GPC | 2027 | 5/1/2027 | ['POSSUM BRANCH', 'YATES COMMON'] | YATES COMMON | Yates Common Substation | 33.4616 | -84.9042 | 80 | [5 empty] | 33.4616 | -84.9042 | MEDIUM | OVERPASS | Rebuild 11.2 miles of 100C 477 ACSR with 200C 1334 T13 ACCR Martin or 200C 1351.0 ACSS between Yates Common to Oak Mountain. Replace limiting elements along the line.
208 | 20771 | CC - GULLATT ROAD TRANSMISSION IMPROVEMENTS | GPC | 2027 | 6/1/2027 | ['GULLATT ROAD TRANSMISSION'] | MORROW | Morrow Substation | 33.6059 | -84.3336 |  | YATES COMMON | Yates Common Substation | 33.4617 | -84.9042 |  | 33.5341 | -84.6191 | MEDIUM | MANUAL | Upstream Transmission improvements to serve a new customer station being built along the Morrow - Yates Common 115kV and Line Creek - Fairburn #2 115kV lines. Rebuild the Morrow - Yates Common 115kV line from Line Creek to the new Gullatt Road customer station. Rebuild the Line Creek - Fairburn #2 115kV line from Line Creek to the new Gullatt Road customer station. Remove the Owens Corning Tap Connection on the Morrow - Yates Common 115kV line and rebuild the line from North Coweta to Str 1. Build new line section from Str 1 to the new Gullatt Road customer station
208 | 18736 | CC - MICROSOFT - SHUGART (CCO06) | GPC | 2027 | 6/1/2027 | ['MICROSOFT', 'SHUGART'] | MICROSOFT | Microsoft, Parkway Circle, East Point, Fulton County, Georgia, 30272, United States | 33.6393 | -84.517 |  | SHUGART | Shugart Park, Cohutta, Whitfield County, Georgia, United States | 34.9601 | -84.9504 |  | 34.2997 | -84.7337 | LOW | NOMINATIM | GPC will rebuild the Line Creek 230kV substation as breaker and a half configuration and connect the Morrow - Yates 230kV line and the Union City - Yates 230kV White line into Line Creek. For the Union City - Yates 230kV Black line, terminate the line from the Yates side into Shugart Farms, and the line from the Union City side into Line Creek. Build two short lines from Line Creek to Shugart Farms (0.3 miles each) with 100C 1351 ACSR Martin conductor.
201 | 20781 | CC - SUMMER LAKE - VILLA RICA 230KV REBUILD (CC IMPROVMNT) | GPC | 2027 | 6/1/2027 | ['SUMMER LAKE', 'VILLA RICA'] | SUMMER LAKE | Summer Lake Dam, Decatur County, Georgia, United States | 30.7625 | -84.6521 |  | VILLA RICA | Villa Rica, Carroll County, Georgia, 30180, United States | 33.7321 | -84.9191 |  | 32.2473 | -84.7856 | LOW | NOMINATIM | Rebuild the 2.5 mile section from Villa Rica to the new East Villa Rica Switching station on the Summer Lake - Villa Rica 230kV line with bundled 200C 1351 ACSS Martin.
208 | 20736 | CC - TA REALTY ELLENWOOD NETWORK IMPROVEMENTS | GPC | 2027 | 6/1/2027 | ['TA REALTY ELLENWOOD NETWORK'] |  |  | 33.6086 | -84.3021 | [6 empty] | 33.6086 | -84.3021 | LOW | MANUAL | Rebuild the ~14.9mi Austin Drive - Morrow 115kV with 200C 1351.5 ACSS Martin. At Austin Drive 115kV, replace the 115/230kV auto transformer along with upgrades other limiting elements at the station.
212 | 20234 | DOYLE - LG&E MONROE 230KV - JACKS CREEK LOOP IN | GPC | 2027 | 6/1/2027 | ['DOYLE', 'E MONROE', 'JACKS CREEK LOOP'] | DOYLE | Doyle Substation | 33.8379 | -83.6988 | 80 | [5 empty] | 33.8379 | -83.6988 | MEDIUM | OVERPASS | Loop in and out the new Jack's Creek 230kV switching station into the Doyle - LG&E Monroe 230kV line. This is coordinated with the East Walton Project (TEAMS #09662).
201 | 20858 | GTC: ADAMSVILLE - BUZZARD ROOST 230KV REBUILD | GTC | 2027 | 6/1/2027 | ['ADAMSVILLE', 'BUZZARD ROOST'] | ADAMSVILLE | Adamsville, Atlanta, Fulton County, Georgia, 10331, United States | 33.7593 | -84.5052 |  | BUZZARD ROOST | Buzzard Roost, Fannin County, Georgia, United States | 34.6704 | -84.2421 |  | 34.2148 | -84.3737 | LOW | NOMINATIM | GTC plans to rebuild 5 miles of line from Buzzard Roost to Boat Rock Road with 200C 1351 ACSS Martin.
201 | 20776 | GTC: DOUGLASVILLE - VILLA RICA 230KV REBUILD (CC IMPROVEMENT) | GTC | 2027 | 6/1/2027 | ['DOUGLASVILLE', 'VILLA RICA'] | DOUGLASVILLE | Douglasville, Douglas County, Georgia, United States | 33.7515 | -84.7477 |  | VILLA RICA | Villa Rica, Carroll County, Georgia, 30180, United States | 33.7321 | -84.9191 |  | 33.7418 | -84.8334 | LOW | NOMINATIM | Rebuild the 2.5 mile section from Villa to the new East Villa Rica Switching station on the Douglasville - Villa Rica 230kV line with bundled 200C 1351 ACSS Martin.
212 | 20778 | GTC: DOYLE - WINDER PRIMARY 230KV LINE JUMPER REPLACEMENT | GTC | 2027 | 6/1/2027 | ['DOYLE', 'WINDER PRIMARY JUMPER REPLACEMENT'] | DOYLE | Doyle Substation | 33.8379 | -83.6988 | 80 | [5 empty] | 33.8379 | -83.6988 | MEDIUM | OVERPASS | Replace the limiting AAC 1033 jumper with AAC 1590 at Doyle on the Doyle - Winder Primary 230kV line.
216 | 19358 | GTC: EAST MOULTRIE - HIGHWAY 112 230 KV LINE | GTC | 2027 | 6/1/2027 | ['EAST MOULTRIE', 'HIGHWAY'] | EAST MOULTRIE | East Moultrie Substation | 31.2422 | -83.7435 | 80 | HIGHWAY | Deerfield / US Highway 9 Substation | 34.0986 | -84.2667 | 80 | 32.6704 | -84.0051 | MEDIUM | OVERPASS | Build a new 27 miles of 230kV line between HWY 112 and East Moultrie substations with 100C 1351 ACSR conductor.
201 | 20505 | GTC: GARRETT RD - V. RICA 230KV LINE RECONDUCTOR (CC NET IM) | GTC | 2027 | 6/1/2027 | ['GARRETT RD', 'V RICA'] | GARRETT RD | Garrett Road, Columbus, Muscogee County, Georgia, 31820, United States | 32.5593 | -84.8245 |  | V RICA | Villa Rica, Carroll County, Georgia, 30180, United States | 33.7321 | -84.9191 |  | 33.1457 | -84.8718 | LOW | NOMINATIM | GTC will reconductor the section from East Villa Rica Switching station to Garrett Rd with 160C 1351 ACSS on 11.5 miles of the Garrett Road - Villa Rica 230kV line. Additionally, the 2.5 miles section from East Villa Rica Switching Station to Villa Rica will be rebuilt with bundled 200C 1351 ACSS Martin.
214 | 19622 | GTC: RIDDLEVILLE BUS REPLACEMENT | GTC | 2027 | 6/1/2027 | ['RIDDLEVILLE REPLACEMENT'] | RIDDLEVILLE | Riddleville Station | 32.9478 | -82.6475 | [6 empty] | 32.9478 | -82.6475 | LOW | MANUAL | GTC will replace the main 115kV bus at Riddleville substation with higher rating.
214 | 20020 | GTC: SOUTH HAZLEHURST - NEW LACY 230KV LINE | GTC | 2027 | 6/1/2027 | ['SOUTH HAZLEHURST', 'LACY'] | SOUTH HAZLEHURST | South Hazlehurst Substation | 31.8107 | -82.5667 | 80 | [5 empty] | 31.8107 | -82.5667 | MEDIUM | OVERPASS | GTC will build a new 230kV transmission line between South Hazlehurst (bus 2) and New Lacy substation (approximately 25 miles) with 100C ACSR 1351 Martin conductor. Do all the necessary upgrade work to accommodate the additional line in both facilities.
201 | 20506 | GTC: SWITCH WAY - THORNTON ROAD 230KV LINE REBUILD | GTC | 2027 | 6/1/2027 | ['SWITCH WAY', 'THORNTON ROAD'] | SWITCH WAY | Switch Way, Mableton, Douglas County, Georgia, 30122, United States | 33.7535 | -84.5876 |  | THORNTON ROAD | Thornton Road, Douglas County, Georgia, 30168, United States | 33.7704 | -84.602 |  | 33.762 | -84.5948 | LOW | NOMINATIM | GTC will rebuild the 1.3 mile Switchway - Thornton Rd 230kV line with 200C 1351 ACSS.
218 | 18668 | JESUP - OFFERMAN 115KV REBUILD | GPC | 2027 | 6/1/2027 | ['JESUP', 'OFFERMAN'] | JESUP | Jesup, Wayne County, Georgia, 31599, United States | 31.6074 | -81.8854 |  | OFFERMAN | Offerman, Pierce County, Georgia, 31556, United States | 31.4097 | -82.1118 |  | 31.5085 | -81.9986 | LOW | NOMINATIM | Rebuild 20 miles of 100C 4/0 ACSR Penguin conductor along the Jesup - Offerman 115kV line, with 100C 795 ACSR Drake conductor.
202 | 10143 | LAWRENCEVILLE - WINDER 115KV LINE REBUILD | GPC | 2027 | 6/1/2027 | ['LAWRENCEVILLE', 'WINDER'] | LAWRENCEVILLE | Lawrenceville, Gwinnett County, Georgia, United States | 33.9566 | -83.989 |  | WINDER | Winder, Barrow County, Georgia, United States | 33.9919 | -83.7184 |  | 33.9743 | -83.8537 | LOW | NOMINATIM | Rebuild approximately 1.2 miles of 100C 636 ACSR conductor from Johns Manville to Winder Primary with 200C 795 ACSS conductor.
202 | 10481 | LAWRENCEVILLE - WINDER PRIMARY 230KV LINE REBUILD | GPC | 2027 | 6/1/2027 | ['LAWRENCEVILLE', 'WINDER PRIMARY'] | WINDER PRIMARY | Winder Primary Substation | 33.9955 | -83.7531 | 80 | [5 empty] | 33.9955 | -83.7531 | MEDIUM | OVERPASS | Rebuild the entire Lawrenceville - Winder Primary 230kV line, approximately 15.4 miles, using 200C 1351 ACSS "Martin" conductor.
215 | 20264 | MEAG: RAY PLACE RD - WARRENTON PRIMARY | MEAG | 2027 | 6/1/2027 | ['RAY PLACE RD', 'WARRENTON PRIMARY'] | WARRENTON PRIMARY | Warrenton Primary Substation | 33.3805 | -82.6873 | 80 | [5 empty] | 33.3805 | -82.6873 | MEDIUM | OVERPASS | Rebuild 10 miles of Ray Place - Warrenton Primary 115kV line with 100C 2 - 1351 ACSR conductor and replace 1590 AAC Coreopsis jumpers at Warrenton.
214 | 19248 | SANDERSVILLE #1 - WADLEY PRI. 115KV REBUILD/RECONDUCTOR | GPC | 2027 | 6/1/2027 | ['SANDERSVILLE', 'WADLEY PRI REBUILD/RECONDUCTOR'] | SANDERSVILLE | Sandersville Substation #1 | 32.9985 | -82.8019 | 80 | [5 empty] | 32.9985 | -82.8019 | MEDIUM | OVERPASS | Rebuild approximately 24.3 miles of the Sandersville #1 - Wadley Primary 115kV line from 100C 336 ACSR Linnet conductor to 100C 1351 ACSR Drake conductor. Replace limiting elements in substations along the line.
219 | 20785 | SAV: GOSHEN (SAV) - KRAFT 115KV LINE REBUILD | SAV | 2027 | 6/1/2027 | ['GOSHEN', 'KRAFT'] | GOSHEN | Goshen, Lincoln County, Georgia, United States | 33.8637 | -82.5079 |  | KRAFT | Rome Kraft Lake Dam, Elbert County, Georgia, United States | 34.1077 | -82.9373 |  | 33.9857 | -82.7226 | LOW | NOMINATIM | Rebuild 9.3 miles of Goshen - Kraft 115kV line from Kraft - Godley J - Rice Hope from 100C 795 ACSR Drake to 200C 1351 ACSS Martin.
219 | 20065 | SAV: GOSHEN (SAV) - MCINTOSH 115KV LINE REBUILD | SAV | 2027 | 6/1/2027 | ['GOSHEN', 'MCINTOSH'] | GOSHEN | Goshen, Lincoln County, Georgia, United States | 33.8637 | -82.5079 |  | MCINTOSH | McIntosh County, Georgia, United States | 31.498 | -81.3922 |  | 32.6809 | -81.95 | LOW | NOMINATIM | Rebuild the Goshen (Savannah) - Georgia Pacific (Rincon) section, approximately 6.7 miles, of the Goshen (Sav) - McIntosh 115kV line using 100C 795 ACSR Drake conductor.
208 | 20717 | CC - TOMOCHICHI 500/230KV SOLUTION (CC NETWORK IMPROVEMENTS) | GPC | 2027 | 7/15/2027 | ['TOMOCHICHI SOLUTION'] |  |  | 33.2825 | -83.9548 | [6 empty] | 33.2825 | -83.9548 | LOW | MANUAL | Build the new Tomochichi 500/230kV switching station (four element ring bus 500kV high side, four element breaker and a half 230kV low side) splitting the Ohara - Schere 500kV line. Build two new 230kV lines from the new Tomochichi substation to the new Towaliga River 230kV substation.
214 | 18573 | GRID - ARKWRIGHT - LLOYD SHOALS 115KV | GPC | 2027 | 7/30/2027 | ['GRID', 'ARKWRIGHT', 'LLOYD SHOALS'] | GRID | Sweet Auburn Market, Jesse Hill Junior Drive Southeast, Sweet Auburn, Old Fourth Ward, Atlanta, Fulton County, Georgia, 30303, United States | 33.7541 | -84.3804 |  | ARKWRIGHT | Arkwright, Macon, Bibb County, Georgia, 31209, United States | 32.9329 | -83.703 |  | 33.3435 | -84.0417 | LOW | NOMINATIM | Rebuild the Arkwright - Lloyd Shoals 115kV line with 100C 795 ACSR Drake.
214 | 20591 | GTC: EATONTON PRIMARY (035591) - LICK CREEK 115KV REBUILD | GTC | 2027 | 12/1/2027 | ['EATONTON PRIMARY', 'LICK CREEK'] | LICK CREEK | Lick Creek, Redbud, Gordon County, Georgia, United States | 34.5397 | -84.8039 | [6 empty] | 34.5397 | -84.8039 | LOW | NOMINATIM | Rebuild approximately 7.5 miles Eatonton Primary - Lick Creek 115kV line section with 100C 795 ACSR conductor.
212 | 17977 | ATHENA - EAST WATKINSVILLE 115 KV (REBUILD) | GPC | 2027 | 12/31/2027 | ['ATHENA', 'EAST WATKINSVILLE'] | ATHENA | Athena Substation | 33.9764 | -83.3461 | 80 | EAST WATKINSVILLE | East Watkinsville Substation | 33.8605 | -83.3848 | 80 | 33.9185 | -83.3654 | MEDIUM | OVERPASS | Rebuild 8.47 miles of the University of Georgia - East Watkinsville line sections on the Athena - East Watkinsville 115kV line with 100C ACSR 1033 conductor.
211 | 20150 | CC - HILL VIEW & GRASSY HOLLOW SUB - CC IMPROVEMENTS | GPC | 2027 | 12/31/2027 | ['HILL VIEW', 'GRASSY HOLLOW'] | HILL VIEW | View Hill Court, Sandy Springs, Fulton County, Georgia, 30350, United States | 33.9865 | -84.3548 |  | GRASSY HOLLOW | Grassy Hollow Road, Cherokee County, Georgia, 03183, United States | 34.2836 | -84.6479 |  | 34.135 | -84.5014 | LOW | NOMINATIM | Build two 230kV switching stations (Hill View and Grassy Hollow) looping into the Cartersville - McGrau Ford 230kV line (8.5 miles apart). Build two new 230kV lines: Cass Pine - Great Valley and Great Valley - Grassy Hollow (total 10.1 miles) with 200C 1351 ACSS Martin.
211 | 20024 | DYER ROAD - EAST ROANOKE 115KV (REBUILD) | GPC | 2027 | 12/31/2027 | ['DYER ROAD', 'EAST ROANOKE'] | DYER ROAD | Dyer Road, Lytle, Fort Oglethorpe, Walker County, Georgia, 30707, United States | 34.9172 | -85.2673 |  | EAST ROANOKE | East Roanoke Drive, Fitzgerald, Ben Hill County, Georgia, 31750, United States | 31.7059 | -83.2535 |  | 33.3115 | -84.2604 | LOW | NOMINATIM | Rebuild 20.7 miles of 75C 397.5 ACSR conductor with advanced conductor from Dyer Road to Wansley tap on the Dyer Road - East Roanoke (APC) 115kV line.
214 | 19997 | AULTMAN ROAD-PERRY 115KV LINE REBUILD | GPC | 2028 | 6/1/2028 | ['AULTMAN ROAD', 'PERRY'] | AULTMAN ROAD | Aultman Road, Fort Valley, Peach County, Georgia, 31008, United States | 32.5623 | -83.7388 |  | PERRY | Perry, Houston County, Georgia, 31069, United States | 32.4587 | -83.732 |  | 32.5105 | -83.7354 | LOW | NOMINATIM | Rebuild the PPG J2 - Langston Road line section of the Aultman Road - Perry 115kV line from 100C 336 ACSR Linnet conductor to 200C 1351 ACSS conductor.
201 | 20797 | CC - EAST VILLA RICA AREA SWITCHING STATION (CC IMPROVEMENT) | GPC | 2028 | 6/1/2028 | ['EAST VILLA RICA AREA SWITCHING STATION'] |  |  | 33.7408 | -84.8554 | [6 empty] | 33.7408 | -84.8554 | LOW | MANUAL | Build a 7 rung breaker and a half switching station along the right of way of the (3) 230kV lines about 2.5 miles East of Villa Rica to service recently signed customers in the area. All three lines will terminate into this station.
211 | 20774 | CC - VILLA RICA UPGRADES (CC NETWORK IMPROVEMENTS) | GPC | 2028 | 6/1/2028 | ['VILLA RICA UPGRADES'] | VILLA RICA UPGRADES | Villa Rica - Pegamore | 33.8786 | -84.8809 | 75 | [5 empty] | 33.8786 | -84.8809 | MEDIUM | OVERPASS | Loop in the Bowen - Union City line into Villa Rica 500kV bus and add a second 2016 MVA 500/230kV auto transformer. Convert the 230kV side to a 10 element breaker and a half scheme.
214 | 21048 | FITZGERALD - PITTS 115 KV LINE REBUILD | GPC | 2028 | 6/1/2028 | ['FITZGERALD', 'PITTS'] | FITZGERALD | Fitzgerald, Ben Hill County, Georgia, 31750, United States | 31.715 | -83.2542 |  | PITTS | Pitts, Wilcox County, Georgia, 31072, United States | 31.9446 | -83.5407 |  | 31.8298 | -83.3975 | LOW | NOMINATIM | Rebuild approximately 26.14 miles of the Fitzgerald - Pitts 115kV line with 200C 1351 ACSS.
213 | 8458 | GTC: BARNESVILLE - SOUTH GRIFFIN 230KV PROJECT | GTC | 2028 | 6/1/2028 | ['BARNESVILLE', 'SOUTH GRIFFIN PROJECT'] | BARNESVILLE | Barnesville, Lamar County, Georgia, 30204, United States | 33.0546 | -84.1557 | [6 empty] | 33.0546 | -84.1557 | LOW | NOMINATIM | Construct 19 miles of 230kV circuit, on existing ROW, using200C 1351 ACSS conductor from South Griffin 230/115kV substation to the Barnesville 230/69kV substation.
216 | 20503 | GTC: BARNEYVILLE - EAST MOULTRIE 115KV NEW LINE | GTC | 2028 | 6/1/2028 | ['BARNEYVILLE', 'EAST MOULTRIE'] | EAST MOULTRIE | East Moultrie Substation | 31.2422 | -83.7435 | 80 | [5 empty] | 31.2422 | -83.7435 | MEDIUM | OVERPASS | Build a new 20 miles of 115kV line with 200C 1351 ACSS from Barneyville to East Moultrie. Add 115kV breakers to Barneyville and East Moultrie substations.
214 | 20873 | GTC: BONAIRE PRIMARY 500/230KV XFMR REPLCMNT & RELAY MOD | GTC | 2028 | 6/1/2028 | ['BONAIRE PRIMARY XFMR REPLCMNT', 'MOD'] | MOD | Hammod Substation | 34.2512 | -85.3456 | 80 | [5 empty] | 34.2512 | -85.3456 | MEDIUM | OVERPASS | Replace 500/230kV, auto transformer C with a new 448 MVA transformer. Replace obsolete relay panels.
212 | 19992 | GTC: BOSTWICK - EAST SOCIAL CIRCLE 230KV RECONDUCTOR | GTC | 2028 | 6/1/2028 | ['BOSTWICK', 'EAST SOCIAL CIRCLE'] | BOSTWICK | Bostwick, Morgan County, Georgia, United States | 33.7374 | -83.5145 |  | EAST SOCIAL CIRCLE | East Elm Street, Social Circle, Walton County, Georgia, 30025, United States | 33.6588 | -83.7146 |  | 33.6981 | -83.6146 | LOW | NOMINATIM | Reconductor 10.8 miles of the East Social Circle - East Watkinsville 230kV line (up to future Bostwick location) from 1033 ACSR Curlew conductor to 1033 ACCR 200C conductor.
206 | 20777 | JACK MCDONOUGH - NORTHWEST (BLACK) 230KV RECONDUCTOR | GPC | 2028 | 6/1/2028 | ['JACK MCDONOUGH', 'NORTHWEST'] | NORTHWEST | Coca-Cola USA Building, 310, North Avenue Northwest, Atlanta, Fulton County, Georgia, 30332, United States | 33.7704 | -84.3979 | [6 empty] | 33.7704 | -84.3979 | LOW | NOMINATIM | Rebuild the Jack McDonough - Northwest (Black) 230kV line (4.59 miles) using 200C 1351 Elbrus/TW.
216 | 19629 | MEAG: BRUMBLEY CREEK - SOUTH BAINBRIDGE 115KV REBUILD | MEAG | 2028 | 6/1/2028 | ['BRUMBLEY CREEK', 'SOUTH BAINBRIDGE'] | BRUMBLEY CREEK | Brumbley Creek, Grady County, Georgia, United States | 30.8823 | -84.1442 |  | SOUTH BAINBRIDGE | South Legette Drive, Bainbridge, Decatur County, Georgia, 31717, United States | 30.8806 | -84.5439 |  | 30.8815 | -84.3441 | LOW | NOMINATIM | Rebuild 2.1 miles segment from line tap into Roddenbery Station on the South Bainbridge - Thomasville 115kV line from 50C ACSR TW 762.8 to 200C 1351 ACSS conductor.
216 | 19630 | MEAG: THOMASVILLE 230/115KV AUTOBANK REPLACEMENT | MEAG | 2028 | 6/1/2028 | ['THOMASVILLE REPLACEMENT'] |  |  | 30.9081 | -84.0051 | [6 empty] | 30.9081 | -84.0051 | HIGH | MANUAL | Replace the 140MVA 230/115kV auto transformer #4 at Thomasville substation.
213 | 20482 | PITTMAN ROAD - WEST POINT DAM (USA) 115KV REBUILD | GPC | 2028 | 6/1/2028 | ['PITTMAN ROAD', 'WEST POINT DAM'] | PITTMAN ROAD | Pittman Road, Holly Brook, South Fulton, Fulton County, Georgia, 30349, United States | 33.6412 | -84.5847 |  | WEST POINT DAM | West Point Dam, Troup County, Georgia, United States | 32.9206 | -85.1905 |  | 33.2809 | -84.8876 | LOW | NOMINATIM | Rebuild 3 miles from the Pittman Road 115kV station to the West Point Dam (USA) 115kV station with 100C 1351 ACSS Martin conductor. Replace AAC 750 jumper at Pittman Road 115kV with (2) 1590 AAC.
208 | 20656 | PLANT YATES BREAKER AND HALF STATION | GPC | 2028 | 6/1/2028 | ['PLANT YATES BREAKER HALF STATION'] | PLANT YATES BREAKER HALF STATION | Plant Yates | 33.4576 | -84.897 | 80 | [5 empty] | 33.4576 | -84.897 | MEDIUM | OVERPASS | Rebuild the Yates 6 & 7 substation to a Breaker and a Half configuration.
219 | 20783 | SAV: COLEMAN - DEAN FOREST 115KV LINE REBUILD | SAV | 2028 | 6/1/2028 | ['COLEMAN', 'DEAN FOREST'] | DEAN FOREST | Dean Forest Substation | 32.0835 | -81.1887 | 80 | [5 empty] | 32.0835 | -81.1887 | MEDIUM | OVERPASS | Rebuild entire line from Coleman to Dean Forest. 6.67 miles of 100C 477 Hawk Conductor with 200C 1351 ACSS Martin conductor.
219 | 20407 | SAV: MAGNOLIA - TRUMAN PARKWAY 115KV REBUILD | SAV | 2028 | 6/1/2028 | ['MAGNOLIA', 'TRUMAN PARKWAY'] | MAGNOLIA | Magnolia, Clinch County, Georgia, United States | 30.8883 | -82.7324 |  | TRUMAN PARKWAY | Harry Truman Parkway, Savannah, Chatham County, Georgia, 31414, United States | 32.0631 | -81.0729 |  | 31.4757 | -81.9027 | LOW | NOMINATIM | Rebuild 3 miles of the Magnolia - Truman Parkway 115kV from 75C 927 ACAR to 200C 1351 ACSS Martin conductor or higher rated conductor. Upgrade 1200A switches at Magnolia substation to 2000A switches and jumpers at Truman Parkway.
201 | 21069 | SMART VALVES AT EAST VILLA RICA SWITCHING STATION | GPC | 2028 | 6/1/2028 | ['SMART VALVES AT EAST VILLA RICA SWITCHING STATION'] |  |  | 33.741 | -84.8556 | [6 empty] | 33.741 | -84.8556 | MEDIUM | MANUAL | Installation of Power Flow Controllers at the new East Villa Rica Switching Station on the Douglasville - Villa Rica 230kV and Summer Lake - Villa Rica 230kV lines. The Power Flow Controllers will be removed when GTCs strategic project at Cavender Drive goes in service.
214 | 20768 | SOUTH MACON 115KV BUSES 1 & 2 REPLACEMENT | GPC | 2028 | 6/1/2028 | ['SOUTH MACON BUSES', 'REPLACEMENT'] |  |  | 32.8204 | -83.6259 | [6 empty] | 32.8204 | -83.6259 | LOW | MANUAL | Replace the 115kV buses 1 and 2 at South Macon with (2) 1590 AAC.
208 | 20274 | UNION CITY - YATES 230KV (BLACK) LINE REBUILD | GPC | 2028 | 6/1/2028 | ['UNION CITY', 'YATES'] | UNION CITY | Union City, Fulton County, Georgia, United States | 33.5871 | -84.5424 |  | YATES | Yates, Coweta County, Georgia, 30275, United States | 33.4634 | -84.8949 |  | 33.5253 | -84.7187 | LOW | NOMINATIM | Rebuild the Union City - Yates 230kV Black line with bundled 200C 1351 ACSS Martin conductor. Replace limiting elements at Union City, Fairburn #1 and Line Creek substations.
213 | 13166 | FIRST AVENUE - NORTH COLUMBUS 115KV LINE REBUILD | GPC | 2028 | 12/1/2028 | ['FIRST AVENUE', 'NORTH COLUMBUS'] | FIRST AVENUE | First Avenue, Tybee Island, Chatham County, Georgia, 31328, United States | 31.9903 | -80.8509 |  | NORTH COLUMBUS | Columbus Body Works North, Veterans Parkway, Nankipooh, Columbus, Muscogee County, Georgia, 31909, United States | 32.5589 | -84.9433 |  | 32.2746 | -82.8971 | LOW | NOMINATIM | Rebuild the 0.9 miles North Columbus - First Avenue 115kV line (currently 75C 657 ACAR) with 200C 1351 ACSS conductor.
214 | 20586 | GTC: NORTH DUBLIN 230/115KV TRANSFORMERS AND BUS-TIE BREAKER | GTC | 2028 | 12/1/2028 | ['NORTH DUBLIN TRANSFORMERS', 'TIE BREAKER'] |  | Dublin Primary Substation | 32.5406 | -82.8945 | [6 empty] | 32.5406 | -82.8945 | MEDIUM | MANUAL | Replace 230/115kV auto transformers A & B with (2) new 230/115kV, 400 MVA auto transformers. Replace 230kV bus tie breaker with a new 2000A breaker. Replace 115kV bus tie breaker with a new 2000A breaker.
208 | 21062 | ASHLEY PARK-WANSLEY 500KV | GPC | 2029 | 6/1/2029 | ['ASHLEY PARK', 'WANSLEY'] | ASHLEY PARK | Ashley Park, Newnan, Coweta County, Georgia, United States | 33.3908 | -84.7644 |  | WANSLEY | Hal B. Wansley Powerplant, Yellow Dirt, Heard County, Georgia, United States | 33.411 | -85.0361 |  | 33.4009 | -84.9003 | LOW | NOMINATIM | Construct a 500kV line from Ashley Park to Wansley, approximately 35 miles long.
216 | 10222 | BLAKELY PRIMARY - HUCKLEBERRY 115KV REBUILD | GPC | 2029 | 6/1/2029 | ['BLAKELY PRIMARY', 'HUCKLEBERRY'] | BLAKELY PRIMARY | Blakely Primary Substation | 31.3716 | -84.906 | 80 | [5 empty] | 31.3716 | -84.906 | MEDIUM | OVERPASS | Rebuild the Blakley Primary - Huckleberry 115kV line from 75C 477 ACSR to 200C 1351 ACSS. (13.5 miles) GPC: Replace jumpers at Blakely Primary GTC: Replace jumpers at Blakely and Huckleberry
214 | 21047 | BROADWAY - ECHECONNEE 115 KV LINE REBUILD | GPC | 2029 | 6/1/2029 | ['BROADWAY', 'ECHECONNEE'] | BROADWAY | Broadway, Tharpe Heights, Macon, Bibb County, Georgia, 31206, United States | 32.7767 | -83.6568 |  | ECHECONNEE | Echeconnee, Houston County, Georgia, 31216, United States | 32.6851 | -83.7005 |  | 32.7309 | -83.6786 | LOW | NOMINATIM | Rebuild the Griffin Rd – Echeconnee line section of Broadway - Echeconnee line with 200C 1351 ACSS conductor.
213 | 16887 | BUTLER - THOMASTON 230KV LINE CONVERSION | GPC | 2029 | 6/1/2029 | ['BUTLER', 'THOMASTON CONVERSION'] | BUTLER | Butler, Taylor County, Georgia, 31006, United States | 32.5571 | -84.2382 | [6 empty] | 32.5571 | -84.2382 | LOW | NOMINATIM | Rebuild the radial Thomaston - Butler 115kV line to 230kV network operation. Make all necessary upgrades and accommodations at Butler and Thomaston. Convert the Wesley substation from 115kV to 230kV.
201 | 21036 | BUZZARD ROOST - FACTORY SHOALS 230KV NEW LINE | GPC | 2029 | 6/1/2029 | ['BUZZARD ROOST', 'FACTORY SHOALS'] | BUZZARD ROOST | Buzzard Roost, Fannin County, Georgia, United States | 34.6704 | -84.2421 |  | FACTORY SHOALS | Factory Shoals Recreation Park, 450, Covington, Newton County, Georgia, 30014, United States | 33.4467 | -83.8283 |  | 34.0585 | -84.0352 | LOW | NOMINATIM | A new 2 mile 230kV line is being built from Buzzard Roost to Factory Shoals with 200C 1351 ACSS Martin conductor.
206 | 21142 | CONYERS - KLONDIKE 230 KV SECOND LINE | GPC | 2029 | 6/1/2029 | ['CONYERS', 'KLONDIKE SECOND'] | CONYERS | Conyers, Rockdale County, Georgia, United States | 33.6676 | -84.0177 | [6 empty] | 33.6676 | -84.0177 | LOW | NOMINATIM | Build a new 6.56 mile line from Conyers to Klondike with 200C (2) 1351 ACSS Martin conductor. Build one new 230kV breaker terminal at Conyers and one new 230kV terminal at Klondike.
206 | 21138 | GLENWOOD SPRINGS - PORTERDALE PRIMARY 230KV LINE SWITCH REPL | GPC | 2029 | 6/1/2029 | ['GLENWOOD SPRINGS', 'PORTERDALE PRIMARY SWITCH REPL'] | GLENWOOD SPRINGS | Old Glenwood Springs Road, Eatonton, Putnam County, Georgia, 31024, United States | 33.3128 | -83.3956 | [6 empty] | 33.3128 | -83.3956 | LOW | NOMINATIM | Replace the 600A line switch at Porterdale Primary on the Glenwood Springs - Porterdale Primary 230kV Line with 1200A switch.
213 | 21112 | GTC: BARNESVILLE PRIMARY - THOMASTON 230KV | GTC | 2029 | 6/1/2029 | ['BARNESVILLE PRIMARY', 'THOMASTON'] | BARNESVILLE PRIMARY | Barnesville Primary Substation | 33.0321 | -84.2013 | 80 | [5 empty] | 33.0321 | -84.2013 | MEDIUM | OVERPASS | Rebuild Barnesville Primary - Thomaston 230kV line (13.24 miles) with 100C 1351 ACSS; Replace 1200A switches at Barnesville Primary & Thomaston with 3000A switch; replace associated jumper at both stations.
202 | 10814 | GTC: BAY CREEK 230/115KV SECOND AUTO TRANSFORMER | GTC | 2029 | 6/1/2029 | ['BAY CREEK SECOND AUTO'] |  |  | 33.8681 | -83.8825 |  | ROCKDALE SUBSTATION |  | 30.6711 | -97.0187 |  | 33.8681 | -83.8825 | LOW | MANUAL | Install a second 230/115kV, 400 MVA auto transformer at the Bay Creek substation.
214 | 21140 | GTC: BONAIRE PRIMARY - EASTMAN PRIMARY 115 KV LINE REBUILD | GTC | 2029 | 6/1/2029 | ['BONAIRE PRIMARY', 'EASTMAN PRIMARY'] | BONAIRE PRIMARY | Bonaire Primary Substation | 32.5648 | -83.6 | 80 | [5 empty] | 32.5648 | -83.6 | MEDIUM | OVERPASS | Rebuild 41.08 miles of the Bonaire Primary - Eastman Primary 115kV Line using 200C 1351ACSS Martin and upgrade the bus at Roddy substation.
201 | 20849 | GTC: CLIFTONDALE - LINE CREEK 230KV LINE | GTC | 2029 | 6/1/2029 | ['CLIFTONDALE', 'CREEK'] | CLIFTONDALE | Cliftondale, South Fulton, Fulton County, Georgia, United States | 33.6448 | -84.5947 |  | CREEK | Creek, Roswell, Fulton County, Georgia, 30077, United States | 34.0122 | -84.3415 |  | 33.8285 | -84.4681 | LOW | NOMINATIM | An 11.6 mile 230kV line is being built form Cliftondale to Line Creek with 200C 1351 ACSS Martin.
213 | 19950 | GTC: DRESDEN - TALBOT 500KV LINE | GTC | 2029 | 6/1/2029 | ['DRESDEN', 'TALBOT'] | DRESDEN | Dresden, Coweta County, Georgia, United States | 33.3515 | -84.9185 |  | TALBOT | Talbot County, Georgia, United States | 32.6985 | -84.5054 |  | 33.025 | -84.712 | LOW | NOMINATIM | GTC will build a new 500kV line from Talbot to Dresden (75 miles). This project will create a new Talbot 500/230kV substation with a 500/230kV auto transformers. The low side of the auto transformers will connect to the Talbot County #1 and #2 230kV buses.
202 | 20760 | GTC: HOPEWELL 230/115 KV BANK A | GTC | 2029 | 6/1/2029 | ['HOPEWELL A'] | HOPEWELL A | Hopewell, Milton, Fulton County, Georgia, 30004, United States | 34.1529 | -84.2855 | [6 empty] | 34.1529 | -84.2855 | LOW | NOMINATIM | Replace the Hopewell 230/115kV auto transformer with a 400 MVA auto transformer.
201 | 21123 | GTC: TENASKA - WANSLEY 500KV NEW LINE | GTC | 2029 | 6/1/2029 | ['TENASKA', 'WANSLEY'] | TENASKA | Tenaska Georgia Substation | 33.3516 | -84.9981 | 80 | [5 empty] | 33.3516 | -84.9981 | MEDIUM | OVERPASS | Construct a 5 mile long 500kV line between Tenaska and Wansley. Make all necessary accommodations at the substations for the line termination.
206 | 21141 | LLOYD SHOALS - PORTERDALE PRIMARY 115KV REBUILD | GPC | 2029 | 6/1/2029 | ['LLOYD SHOALS', 'PORTERDALE PRIMARY'] | LLOYD SHOALS | Lloyd Shoals - North Saddle Dike, Jasper County, Georgia, United States | 33.33 | -83.834 | [6 empty] | 33.33 | -83.834 | LOW | NOMINATIM | Rebuild 15.8 miles of 50C 397.5 ACSR Ibis with 200C 1351 ACSS Martin from Jackson Lake to Lloyd Shoals and Jackson Lake to South. Covington Junction.
216 | 20285 | LOWER RIVER - WEBB (APC) 115KV RECONDUCTOR | GPC | 2029 | 6/1/2029 | ['LOWER RIVER', 'WEBB'] | LOWER RIVER | Lower Little Tallapoosa River Watershed Structure Number 25 Dam, Carroll County, Georgia, 30182, United States | 33.6142 | -85.287 |  | WEBB | Webb, Milton, Fulton County, Georgia, 30005, United States | 34.0973 | -84.2594 |  | 33.8558 | -84.7732 | LOW | NOMINATIM | Reconductor 0.97 miles of 100C 636 Grosbeak Lower River - Webb 115kV line with 200C 795 ACSS Drake conductor.
212 | 19621 | MCEVER ROAD - SHOAL CREEK 115KV REBUILD | GPC | 2029 | 6/1/2029 | ['MCEVER ROAD', 'SHOAL CREEK'] | MCEVER ROAD | McEver Road Substation | 34.2729 | -83.8738 | 80 | [5 empty] | 34.2729 | -83.8738 | MEDIUM | OVERPASS | Rebuild the 636 ACSR (1 mile) of the McEver Road - College Square section, and 2 - 4/0 copper part (2.05 miles) of the College Square to Lakeside WTP B line section, part of the McEver Road - Shoal Creek 115kV line, using 200C 1351 ACSS conductor.
218 | 20346 | MCMANUS - WEST BRUNSWICK 115KV REBUILD | GPC | 2029 | 6/1/2029 | ['MCMANUS', 'WEST BRUNSWICK'] | MCMANUS | Plant McManus | 31.2159 | -81.5441 | 80 | WEST BRUNSWICK | West Brunswick Substation | 31.2799 | -81.5587 | 80 | 31.2479 | -81.5514 | MEDIUM | OVERPASS | Rebuild the McManus - West Brunswick 115kV line, approximately 5.7 miles, with 200C 1351 ACSS Martin conductor.
214 | 17706 | MEAG: AULTMAN ROAD - FORT VALLEY #1 115 KV REBUILD | MEAG | 2029 | 6/1/2029 | ['AULTMAN ROAD', 'FORT VALLEY'] | FORT VALLEY | Fort Valley State University Solar | 32.5015 | -83.8806 | 80 | [5 empty] | 32.5015 | -83.8806 | MEDIUM | OVERPASS | Rebuild approximately 8 miles of the Aultman Road - Fort Valley #1 115kV line with 200C 1351 ACSS conductor.
216 | 11051 | MEAG: SLAPPEY DRIVE - WESTOVER 115KV LINE REBUILD | MEAG | 2029 | 6/1/2029 | ['SLAPPEY DRIVE', 'WESTOVER'] | SLAPPEY DRIVE | Slappey Drive, Coweta County, Georgia, 30277, United States | 33.4343 | -84.6593 |  | WESTOVER | Westover, Albany, Dougherty County, Georgia, 31707, United States | 31.5893 | -84.2113 |  | 32.5118 | -84.4353 | LOW | NOMINATIM | Rebuild 2.92 miles of 100C sagged 477 ACSR Hawk conductor from Slappey Drive to Albany #9 with 1351 ACSR.
202 | 20757 | NORCROSS - NORTH DRUID HILLS 115KV REBUILD | GPC | 2029 | 6/1/2029 | ['NORCROSS', 'NORTH DRUID HILLS'] | NORCROSS | Norcross, Gwinnett County, Georgia, 30071, United States | 33.9412 | -84.2135 |  | NORTH DRUID HILLS | North Druid Hills, Brookhaven, DeKalb County, Georgia, 30329, United States | 33.8206 | -84.3194 |  | 33.8809 | -84.2665 | LOW | NOMINATIM | Rebuild the Norcross - Norcross Junction (674) segment, approximately 3.9 miles, from 100C 477 ACSR Hawk conductor to 200C 1351 ACSS "Martin" conductor.
219 | 21006 | SAV: BOULEVARD - MAGNOLIA 115 KV LINE REBUILD | SAV | 2029 | 6/1/2029 | ['BOULEVARD', 'MAGNOLIA'] | BOULEVARD | Boulevard Substation | 32.0412 | -81.1445 | 80 | [5 empty] | 32.0412 | -81.1445 | MEDIUM | OVERPASS | Rebuild the entire line from Boulevard to Magnolia (4.56 miles) from 100C 795 ACSR Drake to 200C 1351 ACSS Martin
219 | 21023 | SAV: DEAN FOREST - LITTLE OGEECHEE 230 KV REBUILD | SAV | 2029 | 6/1/2029 | ['DEAN FOREST', 'LITTLE OGEECHEE'] | DEAN FOREST | Dean Forest Substation | 32.0835 | -81.1887 | 80 | [5 empty] | 32.0835 | -81.1887 | MEDIUM | OVERPASS | Rebuild the entire line from Little Ogeechee - Salt Creek and Salt Creek - Dean Forest, approximately 8 miles, using 200C 1351 ACSS/Martin. Upgrade jumpers at the Little Ogeechee terminal.
219 | 20989 | SAV: RICE HOPE NEW AUTO TRANSFORMER | SAV | 2029 | 6/1/2029 | ['RICE HOPE AUTO'] |  |  | 32.3475 | -81.1822 | [6 empty] | 32.3475 | -81.1822 | LOW | MANUAL | Install a new 230/115kV 400MVA auto transformer at Rice Hope and loop in the Crossgate - McIntosh 230kV line.
216 | 13628 | SOUTH BAINBRIDGE - SINAI (FPL) 115KV LINE RECONDUCTOR | GPC | 2029 | 6/1/2029 | ['SOUTH BAINBRIDGE', 'SINAI'] | SOUTH BAINBRIDGE | South Legette Drive, Bainbridge, Decatur County, Georgia, 31717, United States | 30.8806 | -84.5439 |  | SINAI | Mount Sinai Baptist Church Cemetery, Bogart, Clarke County, Georgia, United States | 33.953 | -83.524 |  | 32.4168 | -84.034 | LOW | NOMINATIM | Rebuild the Four Mile tap - Recovery - Sinai (FPL) segment of the Sinai (FPL) - South Bainbridge 115kV line from 100C 336.4 ACSR to 200C 1351 ACSS. 9.8 miles in FPL and 13.75 miles in GPC At Recovery (GTC): Replace 100C 336.4 ACSR string bus with higher rating and jumpers with (1) 1590 AAC At Sinai (FPL): Replace 100C 336.4 ACSR string bus with higher rating
202 | 20248 | BAY CREEK - CONYERS 230KV REBUILD | GPC | 2029 | 12/31/2029 | ['BAY CREEK', 'CONYERS'] | BAY CREEK | Bay Creek, Gwinnett County, Georgia, 30017, United States | 33.8826 | -83.9391 |  | CONYERS | Conyers, Rockdale County, Georgia, United States | 33.6676 | -84.0177 |  | 33.7751 | -83.9784 | LOW | NOMINATIM | GPC will rebuild the Bay Creek - Conyers 230kV line, approximately 15.29 miles, using 200C 1351 ACSS "Martin" conductor.
211 | 21129 | ANNISTON - HAMMOND 230KV LINE | GPC | 2030 | 6/1/2030 | ['ANNISTON', 'HAMMOND'] | ANNISTON | Anniston Avenue Southeast, Edgewood, Atlanta, DeKalb County, Georgia, 30317, United States | 33.7517 | -84.3376 |  | HAMMOND | Hammond, Sandy Springs, Fulton County, Georgia, 30328, United States | 33.9254 | -84.3674 |  | 33.8385 | -84.3525 | LOW | NOMINATIM | Rebuild the 28.12 miles section between Hammond and the Goshen tap with 200C 1351 ACSS Martin conductor.
201 | 20764 | ATKINSON - NORTHSIDE DRIVE 115KV REBUILD | GPC | 2030 | 6/1/2030 | ['ATKINSON', 'NORTHSIDE DRIVE'] | ATKINSON | Plant McDonough-Atkinson | 33.8255 | -84.4714 | 80 | [5 empty] | 33.8255 | -84.4714 | MEDIUM | OVERPASS | Rebuild a portion of the Atkinson - Northside 115kV line, approximately 3.2 miles from Atkinson to Chattahoochee with 200C 1351 ACSS Martin.
201 | 20761 | ATKINSON - NORTHWEST 115KV REBUILD | GPC | 2030 | 6/1/2030 | ['ATKINSON', 'NORTHWEST'] | ATKINSON | Plant McDonough-Atkinson | 33.8255 | -84.4714 | 80 | [5 empty] | 33.8255 | -84.4714 | MEDIUM | OVERPASS | Rebuild the 1.2 mile Atkinson - Tilford Yards section of the Atkinson - Northwest 115kV with 200C 1351 ACSS Martin.
212 | 21130 | CC - NORTH GEORGIA DATA NETWORK UPGRADES | GPC | 2030 | 6/1/2030 | ['NORTH GEORGIA DATA NETWORK UPGRADES'] |  |  | 34.1824 | -84.9166 |  | LAWRENCE SMITH |  | 38.6097 | -94.3434 |  | 34.1824 | -84.9166 | HIGH | MANUAL | Construct approximately 7 miles of 115kV line with minimum 170C 1351 ACSS conductor from Gillsville Tap Junction to Midway. Utilize the existing GPC owned North Jackson - Lawrence Smith 46kV ROW that is to be retired. Disconnect the East Maysville 115kV tap at Midway 115kV and terminate the new Pond Fork - Midway 115kV line.
212 | 10478 | CORNELIA - TALLULAH LODGE 115KV REBUILD | GPC | 2030 | 6/1/2030 | ['CORNELIA', 'TALLULAH LODGE'] | CORNELIA | Cornelia, Habersham County, Georgia, United States | 34.5115 | -83.5271 | [6 empty] | 34.5115 | -83.5271 | LOW | NOMINATIM | Rebuild approximately 9.7 miles of the Cornelia - Chase Road - Clarksville - Hollywood segments of the Cornelia - Tallulah Lodge 115kV line with 200C 795 ACSS conductor.
212 | 18669 | DU: DAWSON CROSSING - NELSON (WHITE) 115 KV REBUILD | DU | 2030 | 6/1/2030 | ['DAWSON CROSSING', 'NELSON'] | DAWSON CROSSING | Dawson Crossing Substation | 34.3781 | -84.1336 | 80 | NELSON | Nelson Substation | 34.3866 | -84.3788 | 80 | 34.3824 | -84.2562 | MEDIUM | OVERPASS | Rebuild approximately 15.7 miles of the Dawson Crossing - Etowah - Reavis Mountain - Nelson sections of the Dawson Crossing - Nelson (White) 115kV line with 1351 ACSS conductor. GPC will make any necessary relaying changes at Dawson Crossing.
201 | 21097 | EAST POINT - TRIBUTARY 230KV REBUILD | GPC | 2030 | 6/1/2030 | ['EAST POINT', 'TRIBUTARY'] | EAST POINT | East Point Primary Substation | 33.6763 | -84.463 | 80 | [5 empty] | 33.6763 | -84.463 | MEDIUM | OVERPASS | Rebuild the 2.9 mile section from Cavender Drive to Marietta 25 with 200C 1351 ACSS conductor on the East Point - Tributary 230kV line.
208 | 20480 | EAST POINT - UNION CITY 230KV BLACK LINE RECONDUCTOR | GPC | 2030 | 6/1/2030 | ['EAST POINT', 'UNION CITY BLACK'] | EAST POINT | East Point Primary Substation | 33.6763 | -84.463 | 80 | [5 empty] | 33.6763 | -84.463 | MEDIUM | OVERPASS | Reconductor the 1.5 mile section from Flat Shoals Road station to the Stonewall Tell loop - in point on the East Point - Union City 230kV Black line with 200C 1351 ACSS Martin conductor. Replace limiting elements at Union City
214 | 19627 | ECHECONNEE-WELLSTON 115KV LINE REBUILD | GPC | 2030 | 6/1/2030 | ['ECHECONNEE', 'WELLSTON'] | ECHECONNEE | Echeconnee, Houston County, Georgia, 31216, United States | 32.6851 | -83.7005 |  | WELLSTON | Warner Robins, Houston County, Georgia, United States | 32.6201 | -83.6066 |  | 32.6526 | -83.6535 | LOW | NOMINATIM | Rebuild approximately 11.8 miles of the Echeconnee - Wellston 115kV line with 200C 1351 ACSS conductor and the limiting elements along the line with higher ratings. Replace the Bus at North Warner Robins with 1590 AAC.
216 | 21063 | FARLEY (APC)-TAZEWELL 500KV | GPC | 2030 | 6/1/2030 | ['FARLEY', 'TAZEWELL'] | FARLEY | Raccoon Creek - Farley 500kV | 31.297 | -84.612 | 80 | [5 empty] | 31.297 | -84.612 | MEDIUM | OVERPASS | Construct a new 500kV line from Farley (APC) to Tazewell substation, approximately 120 miles long. Construct a 5 breaker 500kV ring bus to loop in the Blacksmith - Talbot 500kV line, terminate the new Farley - Tazewell 500kV and Talbot #2 - Tazewell 500kV lines. Install a 500/230kV auto transformer to connect to the existing 230kV switchyard.
212 | 12120 | GAINESVILLE #2 - MCEVER ROAD 115 KV REBUILD | GPC | 2030 | 6/1/2030 | ['GAINESVILLE', 'MCEVER ROAD'] | MCEVER ROAD | McEver Road Substation | 34.2729 | -83.8738 | 80 | [5 empty] | 34.2729 | -83.8738 | MEDIUM | OVERPASS | Rebuild approximately 5.3 miles of the Gainesville #2 - McEver Rd 115kV line with 200C 1351 ACSS conductor.
214 | 20298 | GLENWOOD SPRINGS - LAKE OCONEE 115KV LINE REBUILD | GPC | 2030 | 6/1/2030 | ['GLENWOOD SPRINGS', 'LAKE OCONEE'] | GLENWOOD SPRINGS | Old Glenwood Springs Road, Eatonton, Putnam County, Georgia, 31024, United States | 33.3128 | -83.3956 |  | LAKE OCONEE | Lake Oconee, Greene County, Georgia, United States | 33.5046 | -83.2828 |  | 33.4087 | -83.3392 | LOW | NOMINATIM | Rebuild the North Eatonton Junction - Putnam Sawmill Junction line with 200C 1351 ACSS conductor.
213 | 21128 | GOAT ROCK REACTORS INSTALLATION | GPC | 2030 | 6/1/2030 | ['GOAT ROCK REACTORS INSTALLATION'] |  |  | 32.6084 | -85.0825 |  | FORTSON SUBSTATION |  | 32.6108 | -84.9166 |  | 32.6084 | -85.0825 | HIGH | MANUAL | Install 1% series reactors on the Fortson - Goat Rock (Black) 230kV and Fortson - Goat Rock (White) 230kV.
215 | 19996 | GOLDENS CREEK - WARRENTON PRIMARY 230KV REBUILD | GPC | 2030 | 6/1/2030 | ['GOLDENS CREEK', 'WARRENTON PRIMARY'] | WARRENTON PRIMARY | Warrenton Primary Substation | 33.3805 | -82.6873 | 80 | [5 empty] | 33.3805 | -82.6873 | MEDIUM | OVERPASS | Rebuild approximately 0.34 miles of the Goldens Creek - Warrenton Primary 230kV line from 100C 1 - 1351.5 ACSR Martin conductor to 200C 1351 ACCR Martin conductor or equivalent.
214 | 20428 | GORDON-SANDERSVILLE #1 115KV LINE REBUILD (DEEPSTEP-SAND #6) | GPC | 2030 | 6/1/2030 | ['GORDON', 'SANDERSVILLE'] | SANDERSVILLE | Sandersville Substation #1 | 32.9985 | -82.8019 | 80 | [5 empty] | 32.9985 | -82.8019 | MEDIUM | OVERPASS | Rebuild the Deepstep - Robins Spring (7.6 miles) Robins Spring - Kaolin J (2.23mi), and Kaolin J - Sandersville #6 (0.66 miles) line sections of the Gordon - Sandersville #1 115kV line. Rebuild a total of 10.49 miles from 100C 336 ACSR to 100C ACSR 795 conductor.
215 | 21116 | GOSHEN AREA STRATEGIC SOLUTION | GPC | 2030 | 6/1/2030 | ['GOSHEN AREA STRATEGIC SOLUTION'] |  |  | 36.2053 | -86.4649 |  | GOSHEN SUBSTATION |  | 43.3083 | -112.1217 |  | 36.2053 | -86.4649 | MEDIUM | MANUAL | Construct a 230kV switching station on the Waynesboro - Wilson 230kV line and a new 230kV line between the switching station and Goshen, approximately 12.3 miles. Provides an alternate power flow path into Goshen outside of the existing constrained Goshen - Vogtle corridor.
208 | 21073 | GTC: BIG SMARR - TOMOCHICHI 500KV | GTC | 2030 | 6/1/2030 | ['BIG SMARR', 'TOMOCHICHI'] | TOMOCHICHI | Tomochichi United States Court House, West President Street, Savannah Historic District, Savannah, Chatham County, Georgia, 31401, United States | 32.0781 | -81.0929 | [6 empty] | 32.0781 | -81.0929 | LOW | NOMINATIM | Construct a 500kV line from Big Smarr to Tomochichi, approximately 36 miles long. Make the necessary modifications at Big Smarr and Tomochichi to add breakers and terminate the line.
201 | 21014 | GTC: BUZZARD ROOST - CAVENDER DRIVE 230KV NEW LINE | GTC | 2030 | 6/1/2030 | ['BUZZARD ROOST', 'CAVENDER DRIVE'] | BUZZARD ROOST | Buzzard Roost, Fannin County, Georgia, United States | 34.6704 | -84.2421 |  | CAVENDER DRIVE | Cavender Drive, Whitfield County, Georgia, 30720, United States | 34.7294 | -85.0014 |  | 34.6999 | -84.6218 | LOW | NOMINATIM | GTC is building a new 7 mile 230kV line from Cavender Drive to Buzzard Roost with 200C 1351 ACSS Martin.
201 | 21013 | GTC: CAVENDER DRIVE 500/230KV AUTOBANK | GTC | 2030 | 6/1/2030 | ['CAVENDER DRIVE'] | CAVENDER DRIVE | Cavender Drive, Whitfield County, Georgia, 30720, United States | 34.7294 | -85.0014 | [6 empty] | 34.7294 | -85.0014 | LOW | NOMINATIM | GTC will turn Cavender Drive into a 500/230kV station looping in the Villa Rica - Union City 500kV line, installing a 2016 MVA auto transformer.
212 | 20375 | GTC: EAST WATKINSVILLE 230 KV STATION MODIFICATION | GTC | 2030 | 6/1/2030 | ['EAST WATKINSVILLE STATION MODIFICATION'] | EAST WATKINSVILLE STATION MODIFICATION | East Watkinsville Substation | 33.8605 | -83.3848 | 75.8 | [5 empty] | 33.8605 | -83.3848 | MEDIUM | OVERPASS | Replace the 1600A reactors at East Watkinsville on the Russell Dam 230kV line with larger size.
212 | 21111 | GTC: HARTWELL DAM - HARTWELL ENERGY 230KV SERIES REACTORS | GTC | 2030 | 6/1/2030 | ['HARTWELL DAM', 'HARTWELL ENERGY SERIES REACTORS'] | HARTWELL DAM | Hartwell Dam, Hart County, Georgia, United States | 34.358 | -82.8211 | [6 empty] | 34.358 | -82.8211 | LOW | NOMINATIM | GTC: Replace the 1600A series reactors on the Hartwell Dam - Hartwell Energy 230kV line with 3000A.
212 | 21113 | GTC: HARTWELL ENERGY - MIDDLE FORK 230KV LINE | GTC | 2030 | 6/1/2030 | ['HARTWELL ENERGY', 'MIDDLE FORK'] | HARTWELL ENERGY | Hartwell Energy Facility, Hart County, Georgia, United States | 34.3392 | -82.8202 |  | MIDDLE FORK | Middle Fork Broad River, Franklin County, Georgia, United States | 34.4225 | -83.3586 |  | 34.3809 | -83.0894 | LOW | NOMINATIM | Construct a new 230kV line, approx. 35 miles, from Hartwell Energy to Middle Fork with 200C (2) 1351 ACSS conductor. GTC: Expand Hartwell Energy 230kV and Middle Fork 230kV as necessary to install breakers to accept new line termination.
212 | 21131 | GTC: POND FORK - MIDWAY 115KV LINE | GTC | 2030 | 6/1/2030 | ['POND FORK', 'MIDWAY'] | POND FORK | Pond Fork, Hall County, Georgia, 30575, United States | 34.2369 | -83.7186 |  | MIDWAY | Midway, Liberty County, Georgia, 31320, United States | 31.8058 | -81.4307 |  | 33.0214 | -82.5747 | LOW | NOMINATIM | GTC: Construct approximately 6 miles of 115kV line with minimum 170C 1351 ACSS conductor from Gillsville Tap Junction to Pond Fork, utilizing the existing GTC owned portion of the North Jackson - Lawrence Smith 46kV ROW. At Pond Fork, install a second 230/115kV 400MVA auto transformer and terminate the Pond Fork - Midway 115kV line.
214 | 21077 | GTC: ROCKVILLE - TIGER CREEK -WARTHEN 500KV LINES | GTC | 2030 | 6/1/2030 | ['ROCKVILLE', 'TIGER CREEK', 'WARTHEN'] | TIGER CREEK | Tiger Creek Substation | 33.0945 | -82.9816 | 80 | [5 empty] | 33.0945 | -82.9816 | MEDIUM | OVERPASS | Build the new 500kV line from Rockville to Tiger Creek and Tiger Creek to Warthen, approximately 20 miles and 9 miles long respectively. Build a 500kV yard at Tiger Creek and install a 500/230kV auto transformer. Make all necessary accommodations at Warthen and Rockville for the new 500kV breakers.
216 | 21076 | GTC: TALLBOT #2 - TAZEWELL 500KV LINE | GTC | 2030 | 6/1/2030 | ['TALLBOT', 'TAZEWELL'] | TAZEWELL | Tazewell, Marion County, Georgia, United States | 32.3795 | -84.4402 | [6 empty] | 32.3795 | -84.4402 | LOW | NOMINATIM | Build a new 500kV line from Tazewell to Talbot #2, approximately 20 miles. Make all necessary accommodations at Tazewell and Talbot #2 for the new 500kV breakers and line termination.
214 | 21094 | GTC: TIGER CREEK- ROCKVILLE-NORTH SPA 230KV PROJECT | GTC | 2030 | 6/1/2030 | ['TIGER CREEK', 'ROCKVILLE', 'NORTH SPA PROJECT'] | TIGER CREEK | Tiger Creek Substation | 33.0945 | -82.9816 | 80 | [5 empty] | 33.0945 | -82.9816 | MEDIUM | OVERPASS | Build a new 4 - breaker 230kV ring bus at Rockville substation (no auto transformer to be added at this time). Loop in the Eatonton Primary #2 - Wallace Dam 230kV line. Build a new line 230kV line to Tiger Creek. Build a new 230kV line to North Spa.
212 | 20789 | JEFFERSON ROAD - WINDER PRIMARY 115KV REBUILD | GPC | 2030 | 6/1/2030 | ['JEFFERSON ROAD', 'WINDER PRIMARY'] | WINDER PRIMARY | Winder Primary Substation | 33.9955 | -83.7531 | 80 | [5 empty] | 33.9955 | -83.7531 | MEDIUM | OVERPASS | Rebuild approximately 11 miles of the Jefferson Road - Russell - Richardson Street Junction segments of the Jefferson Road - Winder Primary 115kV line with 200C 1351 ACSS Martin conductor.
216 | 20284 | KETTLE CREEK PRIMARY - PINE GROVE PRIMARY 115KV REBUILD | GPC | 2030 | 6/1/2030 | ['KETTLE CREEK PRIMARY', 'PINE GROVE PRIMARY'] | PINE GROVE PRIMARY | Pine Grove Primary Substation | 30.8816 | -83.228 | 80 | [5 empty] | 30.8816 | -83.228 | MEDIUM | OVERPASS | Rebuild approximately 38.04 miles of 50C 4/0 ACSR conductor from the Pine Grove to the Pearson tap using 200C 1351 ACSS conductor.
215 | 21118 | MEAG: ATHENA - WARRENTON 230KV CONVERSION | MEAG | 2030 | 6/1/2030 | ['ATHENA', 'WARRENTON CONVERSION'] | ATHENA | Athena Substation | 33.9764 | -83.3461 | 80 | [5 empty] | 33.9764 | -83.3461 | MEDIUM | OVERPASS | Reconductor/rebuild and convert the 115kV lines from Athena - Union Point - Ray Place Road - Warrenton Primary to 230kV operation. Expand Athena 230kV bus for new line termination, construct 230kV bus at Union Point, and expand 230kV bus at Warrenton Primary for new line termination. Install 230/115kV auto transformers at Union Point Primary and Ray Place Road. Replace limiting network equipment at substations along the line.
201 | 20857 | NEW CAVENDER DRIVE - TRIBUTARY 230KV LINE | GPC | 2030 | 6/1/2030 | ['CAVENDER DRIVE', 'TRIBUTARY'] | CAVENDER DRIVE | Cavender Drive, Whitfield County, Georgia, 30720, United States | 34.7294 | -85.0014 |  | TRIBUTARY | Tributary, Douglasville, Douglas County, Georgia, United States | 33.7129 | -84.6426 |  | 34.2212 | -84.822 | LOW | NOMINATIM | Build a new 4 mile 230kV line from Cavender Drive to Tributary with 200C 1351 ACSS Martin.
214 | 21093 | NORTH SPA 230KV STRATEGIC PROJECT | GPC | 2030 | 6/1/2030 | ['NORTH SPA STRATEGIC PROJECT'] |  |  | 39.784 | -86.3048 | [6 empty] | 39.784 | -86.3048 | HIGH | MANUAL | This project includes the following scope of work: Build a new 230kV switching station north of Oasis in a ring bus configuration with 4 - breakers. Loop in the East Social Circle - Oasis (White) 230kV line. Build a new 230kV line to Cornish Mountain from North Spa. New 230kV line from Rockville 230kV will terminate in this station.
212 | 19995 | TALLULAH LODGE - TOCCOA 115 KV REBUILD | GPC | 2030 | 6/1/2030 | ['TALLULAH LODGE', 'TOCCOA'] | TOCCOA | Toccoa Primary Substation | 34.5809 | -83.3527 | 80 | [5 empty] | 34.5809 | -83.3527 | MEDIUM | OVERPASS | Rebuild the Tallulah Lodge - Toccoa 115kV Line with 100C 795 ACSR conductor (total of 10.3 miles). Replace limiting elements at Tallulah Lodge and Toccoa.
201 | 21098 | TRIBUTARY - THORNTON RD 230KV REBUILD | GPC | 2030 | 6/1/2030 | ['TRIBUTARY', 'THORNTON RD'] | TRIBUTARY | Tributary, Douglasville, Douglas County, Georgia, United States | 33.7129 | -84.6426 |  | THORNTON RD | Thornton Road, Douglas County, Georgia, 30168, United States | 33.7704 | -84.602 |  | 33.7417 | -84.6223 | LOW | NOMINATIM | Rebuild the 2.8 mile Tributary - Thornton Road 230kV line with 200C 1351 ACSS Martin.
213 | 20160 | THOMASTON 230 NEW BUILD SUB | GPC | 2030 | 11/1/2030 | ['THOMASTON BUILD'] |  |  | 32.8999 | -84.3127 | [6 empty] | 32.8999 | -84.3127 | MEDIUM | MANUAL | Replace Thomaston 230/115kV 285MVA auto transformers C and D with 400MVA auto transformers. Install high side breakers to meet the 230kV bus differential standards and redesign 230kV bus to a breaker and a half configuration.
216 | 18848 | BAINBRIDGE TRANSMISSION: EAST RIVER ROAD, EAST BAINBRIDGE | GPC | 2030 | 12/31/2030 | ['BAINBRIDGE TRANSMISSION', 'EAST RIVER ROAD EAST BAINBRIDGE'] | EAST RIVER ROAD EAST BAINBRIDGE | East River Road, Bainbridge, Decatur County, Georgia, 39817, United States | 30.9235 | -84.556 | [6 empty] | 30.9235 | -84.556 | LOW | NOMINATIM | This project will construct a new 115kV breaker and a half substation a mile north of the East Bainbridge substation. East Bainbridge will be simplified to a 115kV straight bus with two transmission lines for service to load, a generation interconnection point and a capacitor bank.
214 | 19626 | GLENWOOD SPRINGS 115KV CAP BANK | GPC | 2030 | 12/31/2030 | ['GLENWOOD SPRINGS CAP'] |  | Old Glenwood Springs Road, Eatonton, Putnam County, Georgia, 31024, United States | 33.3128 | -83.3956 | [6 empty] | 33.3128 | -83.3956 | HIGH | MANUAL | Install a 115kV two stage 30MVAR capacitor bank at Glenwood Springs substation.
208 | 20690 | EAST POINT - UNION CITY (WHITE) 230KV REBUILD | GPC | 2031 | 5/1/2031 | ['EAST POINT', 'UNION CITY'] | EAST POINT | East Point Primary Substation | 33.6763 | -84.463 | 80 | [5 empty] | 33.6763 | -84.463 | MEDIUM | OVERPASS | Rebuild 5.49 miles of 100C 1590.0 ACSR Lapwing with 200C 1351.5 ACSS Martin 230kV line from Welcome All to Union City on the East Point - Union City 230kV line.
202 | 19632 | AVERY - HOPEWELL 115KV RECONDUCTOR | GPC | 2031 | 6/1/2031 | ['AVERY', 'HOPEWELL'] | AVERY | Avery, Cherokee County, Georgia, 30115, United States | 34.1957 | -84.4224 |  | HOPEWELL | Hopewell, Milton, Fulton County, Georgia, 30004, United States | 34.1529 | -84.2855 |  | 34.1743 | -84.354 | LOW | NOMINATIM | Reconductor the Hopewell to Birmingham line section (approximately 3.3 miles) on the Avery - Hopewell 115kV line with 100C 1033 ACSR conductor. Replace jumper at Birmingham with 1590 AAC jumper.
211 | 10811 | BOWEN #10 500/230KV AUTOBANK REPLACEMENT | GPC | 2031 | 6/1/2031 | ['BOWEN REPLACEMENT'] |  |  | 34.1263 | -84.9186 | [6 empty] | 34.1263 | -84.9186 | HIGH | MANUAL | Replace the existing Bowen #10 1350 MVA 500/230kV auto transformer with a 2016 MVA 500/230kV auto transformer.
215 | 20756 | HATCH - WADLEY 500 KV LINE STRATEGIC PROJECT | GPC | 2031 | 6/1/2031 | ['HATCH', 'WADLEY STRATEGIC PROJECT'] | HATCH | Hatch Nuclear Power Plant, Appling County, Georgia, United States | 31.9322 | -82.3445 | [6 empty] | 31.9322 | -82.3445 | LOW | NOMINATIM | Construct a new 500kV line from Hatch - Wadley Primary.
214 | 21099 | MEAG: PIO NONO 230/115KV AREA SOLUTION | MEAG | 2031 | 6/1/2031 | ['PIO NONO AREA SOLUTION'] |  |  | 38.5998 | -90.3176 | [6 empty] | 38.5998 | -90.3176 | LOW | MANUAL | Build a 4 - breaker 230kV ring bus to terminate lines from Dorsett, South Griffin, and Big Grocery. Install a 400MVA auto transformer and build a 115kV yard to terminate a line from Broadway. Make all necessary modifications to accommodate all the 230kV and 115kV lines terminations.
213 | 21114 | MEAG: SOUTH GRIFFIN 230/115KV BANK #5 | MEAG | 2032 | 6/1/2032 | ['SOUTH GRIFFIN'] | SOUTH GRIFFIN | Alvin Griffin Irrigation Pond Dam South, Ben Hill County, Georgia, United States | 31.7776 | -83.396 | [6 empty] | 31.7776 | -83.396 | LOW | NOMINATIM | Replace 230/115kV 285MVA auto transformer #5 with 230/115kV 400MVA auto transformer at South Griffin.
219 | 20784 | SAV: COLEMAN - MELDRIM 115KV LINE REBUILD | SAV | 2032 | 6/1/2032 | ['COLEMAN', 'MELDRIM'] | COLEMAN | Coleman, Randolph County, Georgia, United States | 31.67 | -84.8906 |  | MELDRIM | Meldrim, Effingham County, Georgia, 31318, United States | 32.1433 | -81.3779 |  | 31.9066 | -83.1342 | LOW | NOMINATIM | Rebuild 3 miles of the Coleman - Meldrim 115kV line from Four Lakes to Meldrim with 200C 1351 ACSS.
214 | 20767 | ARKWRIGHT BUS AND JUMPER REPLACEMENT | GPC | 2033 | 6/1/2033 | ['ARKWRIGHT JUMPER REPLACEMENT'] |  |  | 32.9222 | -83.7261 | [6 empty] | 32.9222 | -83.7261 | HIGH | MANUAL | Replace the 115kV bus at Arkwright with higher rating and replace the jumper on the Arkwright - Forrest Rd (Macon) 115kV line with at least 1590AAC.
202 | 20758 | BAY CREEK - CONYERS 230KV LIMITING ELEMENT REPLACEMENT | GPC | 2033 | 6/1/2033 | ['BAY CREEK', 'CONYERS LIMITING ELEMENT REPLACEMENT'] | BAY CREEK | Bay Creek, Gwinnett County, Georgia, 30017, United States | 33.8826 | -83.9391 | [6 empty] | 33.8826 | -83.9391 | LOW | NOMINATIM | Replace equipment such as jumpers, switches, and traps at the Bay Creek, Rockdale, and Conyers substations with equipment capable of carrying 3000A.
215 | 20793 | EVANS PRIMARY - THURMOND DAM (USA) #5 115KV REBUILD | GPC | 2033 | 6/1/2033 | ['EVANS PRIMARY', 'THURMOND DAM'] | EVANS PRIMARY | Evans Primary Substation | 33.544 | -82.1686 | 80 | [5 empty] | 33.544 | -82.1686 | MEDIUM | OVERPASS | Rebuild approximately 5.45 miles of Euchee Creek - Thurmond Dam segment of the Evans Primary - Thurmond Dam (USA) #5 115kV line with 200C 1351 ACSS Martin conductor. Replace the main bus with a larger element at Thurmond Dam (USA).
215 | 20794 | EVANS PRIMARY - THURMOND DAM (USA) #6 115KV REBUILD | GPC | 2033 | 6/1/2033 | ['EVANS PRIMARY', 'THURMOND DAM'] | EVANS PRIMARY | Evans Primary Substation | 33.544 | -82.1686 | 80 | [5 empty] | 33.544 | -82.1686 | MEDIUM | OVERPASS | Rebuild approximately 8.9 miles of the Evans Primary - Thurmond Dam (USA) #6 115kV line with 200C 1351 ACSS Martin conductor. Replace the main bus with a larger element at Thurmond Dam (USA).
212 | 12217 | GTC: CENTER PRIMARY - CLARKSBORO 230 KV REBUILD | GTC | 2033 | 6/1/2033 | ['CENTER PRIMARY', 'CLARKSBORO'] | CENTER PRIMARY | Center Primary Substation | 34.0534 | -83.3981 | 80 | [5 empty] | 34.0534 | -83.3981 | MEDIUM | OVERPASS | GTC to rebuild the Center Primary – Clarksboro Primary 230kV line (approx. 8.3 miles) with 200C 1351 ACSS conductor.
212 | 20773 | GTC: CLARKSBORO - WINDER PRIMARY 230KV REBUILD | GTC | 2033 | 6/1/2033 | ['CLARKSBORO', 'WINDER PRIMARY'] | WINDER PRIMARY | Winder Primary Substation | 33.9955 | -83.7531 | 80 | [5 empty] | 33.9955 | -83.7531 | MEDIUM | OVERPASS | Rebuild approximately 14 miles of the Clarksboro - Winder 230kV line with 200C 1351 ACSS conductor.
212 | 12147 | GTC: EAST SOCIAL CIRCLE - SNELLVILLE 230KV EQUIPMENT UPGRADE | GTC | 2033 | 6/1/2033 | ['EAST SOCIAL CIRCLE', 'SNELLVILLE EQUIPMENT'] | EAST SOCIAL CIRCLE | East Elm Street, Social Circle, Walton County, Georgia, 30025, United States | 33.6588 | -83.7146 | [6 empty] | 33.6588 | -83.7146 | LOW | NOMINATIM | Replace the 1200A switches at Snellville Primary with 3000A. Also, replace the 1200A line trap and switches at East Social Circle with 3000A on the East Social Circle - Snellville 230kV line.
212 | 21075 | GTC: EAST WALTON - MIDDLE FORK 500KV | GTC | 2033 | 6/1/2033 | ['EAST WALTON', 'MIDDLE FORK'] | EAST WALTON | East Walton Street, Milledgeville, Baldwin County, Georgia, 31061, United States | 33.0919 | -83.2257 |  | MIDDLE FORK | Middle Fork Broad River, Franklin County, Georgia, United States | 34.4225 | -83.3586 |  | 33.7572 | -83.2921 | LOW | NOMINATIM | Construct a new 500kV line from East Walton to Middle Fork, approximately 45 miles long. Make all necessary accommodations for new 500kV breakers at East Walton and Middle Fork substations.
212 | 20791 | GTC: SHOAL CREEK - SOUTH HALL 230KV REBUILD | GTC | 2033 | 6/1/2033 | ['SHOAL CREEK', 'SOUTH HALL'] | SHOAL CREEK | Shoal Creek, Gratis, Walton County, Georgia, 30656, United States | 33.8766 | -83.6685 |  | SOUTH HALL | South Hall, Darlington Drive Southwest, Darlington Square, Rome, Floyd County, Georgia, 30161, United States | 34.2248 | -85.185 |  | 34.0507 | -84.4267 | LOW | NOMINATIM | Rebuild approximately 7.9 miles of South Hall - Chestnut Mountain - Spout Springs Road segments of the Shoal Creek - South Hall 230kV line with 200C 1351 ACSS conductor. Also, replace 1 - AAC 1590 jumpers at South Hall with 2 - AAC 1590.
212 | 21053 | MCEVER ROAD - SHOAL CREEK 115KV REBUILD PHASE III | GPC | 2033 | 6/1/2033 | ['MCEVER ROAD', 'SHOAL CREEK III'] | MCEVER ROAD | McEver Road Substation | 34.2729 | -83.8738 | 80 | [5 empty] | 34.2729 | -83.8738 | MEDIUM | OVERPASS | Rebuild the 2 - 4/0 copper part (approximately 2.9 miles) of the Gainesville Ferry - Lakeside WTP A line section, part of the McEver Road - Shoal Creek 115kV line, using 200C 1351 ACSS conductor.
212 | 9661 | MCGRAU FORD - MIDDLE FORK 500KV LINE PROJECT | GPC | 2033 | 6/1/2033 | ['MCGRAU FORD', 'MIDDLE FORK PROJECT'] | MCGRAU FORD | Mostellar Springs - McGrau Ford 500kV | 34.3571 | -84.6102 | 80 | [5 empty] | 34.3571 | -84.6102 | MEDIUM | OVERPASS | Construct a new approximately 64 mile 500kV line from McGrau Ford to Middle Fork.
219 | 20796 | SAV: MELDRIM BANK D REPLACEMENT | SAV | 2033 | 6/1/2033 | ['MELDRIM D REPLACEMENT'] |  |  | 32.1553 | -81.3682 | [6 empty] | 32.1553 | -81.3682 | HIGH | MANUAL | Replace 300 MVA 230/115kV Bank D with 400 MVA Bank.
215 | 14222 | THOMSON PRIMARY 230/115KV SECOND TRANSFORMER | GPC | 2033 | 6/1/2033 | ['THOMSON PRIMARY SECOND'] |  |  | 35.7951 | -86.898 | [6 empty] | 35.7951 | -86.898 | LOW | MANUAL | Install a second 400 MVA, 230/115kV auto transformer at Thomson Primary substation.
202 | 20759 | WINDER PRIMARY 230KV BUS 1-2 PARALLEL BUS-TIE INSTALLATION | GPC | 2033 | 6/1/2033 | ['WINDER PRIMARY', 'PARALLEL', 'TIE INSTALLATION'] | WINDER PRIMARY | Winder Primary Substation | 33.9955 | -83.7531 | 80 | [5 empty] | 33.9955 | -83.7531 | MEDIUM | OVERPASS | Install a 2nd 230kV bus - tie breaker at the Winder Primary Station.
216 | 10487 | PINE GROVE PRIMARY - WEST VALDOSTA 115 KV RECONDUCTOR | GPC | 2033 | 12/31/2033 | ['PINE GROVE PRIMARY', 'WEST VALDOSTA'] | PINE GROVE PRIMARY | Pine Grove Primary Substation | 30.8816 | -83.228 | 80 | [5 empty] | 30.8816 | -83.228 | MEDIUM | OVERPASS | Rebuild 3.7 miles of 100C 4/0 ACSR conductor with 200C 795 ACSS Drake on the Bemis - Pine Grove Primary section of the Pine Grove Primary - West Valdosta 115kV line.
212 | 18700 | DAWSON CROSSING - GAINESVILLE #1 115 KV | GPC | 2034 | 6/1/2034 | ['DAWSON CROSSING', 'GAINESVILLE'] | DAWSON CROSSING | Dawson Crossing Substation | 34.3781 | -84.1336 | 80 | [5 empty] | 34.3781 | -84.1336 | MEDIUM | OVERPASS | Replace the 500CU main bus at Gainesville #1 115kV with 3" Sch 40 AL Tube.
219 | 20787 | SAV: LITTLE OGEECHEE 230/115KV BANK REPLACEMENT | SAV | 2034 | 6/1/2034 | ['LITTLE OGEECHEE REPLACEMENT'] |  |  | 32.0067 | -81.2532 | [6 empty] | 32.0067 | -81.2532 | HIGH | MANUAL | Replace SATX 280MVA auto transformer with 400MVA auto transformer.
215 | 17993 | EVANS PRIMARY - THOMSON PRIMARY 115KV REBUILD | GPC | 2034 | 12/31/2034 | ['EVANS PRIMARY', 'THOMSON PRIMARY'] | EVANS PRIMARY | Evans Primary Substation | 33.544 | -82.1686 | 80 | THOMSON PRIMARY | Thomson Primary Substation | 33.454 | -82.4142 | 80 | 33.499 | -82.2914 | MEDIUM | OVERPASS | Rebuild the existing 100C 336 ACSR conductor for the Thomson Primary to Pumpkin Center 115kV line section (approximately 5.28 miles), part of the Evans Primary - Thomson Primary 115kV line with 200C 1351 ACSS Martin conductor.